## TITLE PAGE
Water Resources Planning Tables 2019
v11 - August 2016 integrating updates up to v15 - June 2018
All queries on the content of this workbook should be sent to:
water-company-plan@environment-agency.gov.uk
Water resource zone information
Company: |  | Severn Trent Water
Resource Zone Name: |  | North Staffordshire |  |  |  | Data validation: Cell D20
Resource Zone Number: |  | 7 |  |  |  | Dry Year Annual Average
Planning Scenario Name: |  | Dry Year Annual Average | DYAA | Normal Year Annual Average |  | Dry Year Critical Period
Chosen Level of Service: |  | No more than 3 in 100 Temporary Use Bans |  |  |  | Dry Year Annual Average - benchmarking data
Base Year: |  | 2016-17 |  |  |  | Dry Year Critical Period - benchmarking data
Responsible Officer: |  | Marcus O'Kane | Signed: | Marcus O'Kane | Dated:
Version: |  | 1 |  | [Digital signature is acceptable]
Key to cells
Clear cells - indicate an input is required
Yellow shaded cells - indicates a formula.
Blue shaded cells - indicate base year data.
Light grey shaded cells - indicate preceding years.
Dark grey cells - indicate that no data entry is required.
Worksheet |  | Content
WRZ summary |  | Supply-Demand Balance and components
1. BL Licences |  | Baseline water resources
2. BL Supply |  | Baseline water supplies
3. BL Demand |  | Baseline demand
4. BL SDB |  | Baseline supply demand balance
5. Feasible options |  | Fixed and Variable costs, Net Present Value, AIC and AISC of all feasible options - confidential
6. Preferred options |  | High level costs of preferred options (Dry Year) - publicly available
7. FP Supply |  | Final Planning water supplies (impact of Scenario options)
8. FP Demand |  | Final Planning demand (impact of Scenario options)
9. FP SDB |  | Final Planning supply demand balance
10. Drought plan links |  | Drought plan links
11. Drought plan links graph |  | Drought plan links graph

## WRZ summary
Summary graphs of water resources planning tables data
DERIVATION | DESCRIPTION | UNITS | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
SUPPLY
13BL | Total water available for use | Ml/d | 131.2671 | 131.2671 | 131.2671 | 131.2671 | 129.6671 | 129.2671 | 128.8671 | 128.4671 | 128.0671 | 91.6671 | 91.2671 | 90.8671 | 90.4671 | 90.0671 | 89.7671 | 89.6671 | 89.5671 | 89.4671 | 89.3671 | 89.2671 | 89.1671 | 89.0671 | 88.9671 | 88.8671 | 88.7671 | 88.6671 | 88.5671 | 88.4671 | 88.3671
13FP | Total water available for use | Ml/d | 131.2671 | 131.2671 | 131.2671 | 131.2671 | 129.6671 | 129.2671 | 128.8671 | 128.4671 | 128.0671 | 127.6671 | 127.2671 | 126.8671 | 126.4671 | 126.0671 | 125.7671 | 125.6671 | 125.5671 | 125.4671 | 125.3671 | 132.2671 | 132.1671 | 132.0671 | 131.9671 | 131.8671 | 131.7671 | 131.6671 | 131.5671 | 131.4671 | 131.3671
| DEMAND |  | 0
26BL | Unmeasured household consumption | Ml/d | 42.8391 | 41.9019 | 40.9749 | 40.0872 | 39.1836 | 38.332 | 37.5123 | 36.715 | 35.946 | 35.1971 | 34.4701 | 33.7617 | 33.0761 | 32.4035 | 31.7336 | 31.0702 | 30.4147 | 29.7754 | 29.1492 | 28.564 | 27.9939 | 27.4362 | 26.8876 | 26.3522 | 25.8278 | 25.3144 | 24.8133 | 24.3226 | 23.8057
26FP | Unmeasured household consumption | Ml/d | 42.8391 | 41.9019 | 40.9749 | 40.0872 | 39.1836 | 38.332 | 31.8323 | 16.065 | -4.885e-15 | -3.5527e-15 | 0 | 4.885e-15 | 0 | -6.2172e-15 | 0 | 0 | 0 | -3.5527e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25BL | Measured household consumption | Ml/d | 24.129 | 24.9018 | 25.6586 | 26.4346 | 27.1431 | 27.8733 | 28.6125 | 29.3442 | 30.0791 | 30.8108 | 31.5366 | 32.258 | 32.9791 | 33.6893 | 34.2657 | 34.8411 | 35.3916 | 35.9308 | 36.4546 | 37.0164 | 37.5728 | 38.1192 | 38.6495 | 39.1727 | 39.6853 | 40.1881 | 40.6852 | 41.173 | 41.6941
25FP | Measured household consumption | Ml/d | 24.129 | 24.9018 | 25.6586 | 26.4346 | 26.9994 | 27.5631 | 33.4277 | 47.6547 | 62.2073 | 62.3551 | 62.5646 | 62.796 | 63.0294 | 63.252 | 63.2883 | 63.3204 | 63.3596 | 63.3788 | 63.3954 | 63.482 | 63.5878 | 63.6766 | 63.7676 | 63.8555 | 63.9525 | 64.1412 | 64.342 | 64.4349 | 64.2802
23BL+24BL | Non-household consumption | Ml/d | 21.7903 | 21.815 | 21.8001 | 21.8263 | 21.8068 | 21.9193 | 21.9917 | 22.0605 | 22.0514 | 22.1343 | 22.1534 | 22.1721 | 22.1309 | 22.2074 | 22.2292 | 22.2524 | 22.2138 | 22.2909 | 22.3056 | 22.3194 | 22.2717 | 22.348 | 22.3662 | 22.3853 | 22.345 | 22.4261 | 22.4478 | 22.4701 | 22.4328
23FP+24FP | Non-household consumption | Ml/d | 21.7903 | 21.815 | 21.8001 | 21.8263 | 21.8068 | 21.9193 | 21.9917 | 22.0605 | 22.0514 | 22.1343 | 22.1534 | 22.1721 | 22.1309 | 22.2074 | 22.2292 | 22.2524 | 22.2138 | 22.2909 | 22.3056 | 22.3194 | 22.2717 | 22.348 | 22.3662 | 22.3853 | 22.345 | 22.4261 | 22.4478 | 22.4701 | 22.4328
40BL | Total leakage | Ml/d | 29.86 | 29.71 | 29.56 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41
40FP | Total leakage | Ml/d | 29.86 | 29.71 | 29.56 | 29.41 | 29.41 | 29.41 | 29.367 | 29.2532 | 29.1435 | 28.5277 | 27.6454 | 26.7631 | 25.8808 | 24.9985 | 24.2485 | 23.4986 | 22.7486 | 21.9987 | 21.2487 | 20.8238 | 20.3988 | 19.9738 | 19.5488 | 19.1239 | 18.7414 | 18.3589 | 17.9764 | 17.5939 | 17.2115
11BL-(23BL:26BL)-40BL | Other components of demand | Ml/d | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506
11FP-(23FP:26FP)-40FP | Other components of demand | Ml/d | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506 | 3.6506
| Total demand + target headroom (baseline) | Ml/d | 126.7013 | 126.4559 | 126.126 | 125.966 | 125.9586 | 125.9999 | 126.0419 | 126.5392 | 126.6793 | 125.9593 | 126.233 | 126.6822 | 126.8974 | 127.5044 | 127.7424 | 127.6121 | 127.655 | 127.6572 | 127.6191 | 127.6916 | 127.6799 | 127.9719 | 128.2542 | 128.2607 | 128.3947 | 128.7988 | 129.1357 | 129.6161 | 130.1711
| Total demand + target headroom (final plan) | Ml/d | 126.7013 | 126.4559 | 126.126 | 125.966 | 125.8149 | 125.6898 | 125.1342 | 124.043 | 122.5949 | 121.4241 | 121.0263 | 120.8116 | 120.3424 | 120.2521 | 119.8699 | 119.1099 | 118.5469 | 117.9185 | 117.2494 | 117.0069 | 116.6896 | 116.6569 | 116.6235 | 116.305 | 116.1655 | 116.3864 | 116.5456 | 116.7393 | 116.753
SUPPLY-DEMAND BALANCE
16BL | Target headroom | Ml/d | 4.4322 | 4.4766 | 4.4817 | 4.5572 | 4.7644 | 4.8147 | 4.8648 | 5.3589 | 5.5421 | 4.7564 | 5.0122 | 5.4298 | 5.6506 | 6.1436 | 6.4532 | 6.3879 | 6.5742 | 6.5994 | 6.6491 | 6.7311 | 6.7808 | 7.0079 | 7.2902 | 7.2897 | 7.476 | 7.8097 | 8.1288 | 8.5897 | 9.1779
16FP | Target headroom | Ml/d | 4.4322 | 4.4766 | 4.4817 | 4.5572 | 4.7644 | 4.8147 | 4.8648 | 5.3589 | 5.5421 | 4.7564 | 5.0122 | 5.4298 | 5.6506 | 6.1436 | 6.4532 | 6.3879 | 6.5742 | 6.5994 | 6.6491 | 6.7311 | 6.7808 | 7.0079 | 7.2902 | 7.2897 | 7.476 | 7.8097 | 8.1288 | 8.5897 | 9.1779
17BL | Available headroom | Ml/d | 8.998 | 9.2877 | 9.6228 | 9.8584 | 8.4729 | 8.0818 | 7.69 | 7.2868 | 6.9299 | -29.5358 | -29.9537 | -30.3853 | -30.7797 | -31.2937 | -31.5221 | -31.5572 | -31.5137 | -31.5906 | -31.6029 | -31.6934 | -31.732 | -31.8969 | -31.9969 | -32.1038 | -32.1516 | -32.3221 | -32.4398 | -32.5592 | -32.6261
17FP | Available headroom | Ml/d | 8.998 | 9.2877 | 9.6228 | 9.8584 | 8.6166 | 8.392 | 8.5977 | 9.783 | 11.0143 | 10.9994 | 11.253 | 11.4852 | 11.7753 | 11.9586 | 12.3504 | 12.9451 | 13.5944 | 14.1481 | 14.7667 | 21.9913 | 22.2582 | 22.418 | 22.6338 | 22.8518 | 23.0776 | 23.0903 | 23.1503 | 23.3175 | 23.792
Baseline Supply-Demand Balance:
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| SDB (Ml/d) | 3.7085 | 3.2672 | 2.8252 | 1.9279 | 1.3878 | -34.2922 | -34.9659 | -35.8151 | -36.4303 | -37.4373 | -37.9753 | -37.945 | -38.0879 | -38.1901 | -38.252 | -38.4245 | -38.5128 | -38.9048 | -39.2871 | -39.3936 | -39.6276 | -40.1317 | -40.5686 | -41.149 | -41.804
Final Planning Supply-Demand Balance:
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| SDB (Ml/d) | 3.8522 | 3.5773 | 3.7329 | 4.4241 | 5.4722 | 6.243 | 6.2408 | 6.0555 | 6.1247 | 5.815 | 5.8972 | 6.5572 | 7.0202 | 7.5486 | 8.1177 | 15.2602 | 15.4775 | 15.4102 | 15.3436 | 15.5621 | 15.6016 | 15.2807 | 15.0215 | 14.7278 | 14.6141
| Company: | 2026-27: Severn Trent Water
| Resource Zone Name | 2026-27: North Staffordshire
| Resource Zone Number: | 2026-27: 7
| Planning Scenario Name: | 2026-27: Dry Year Annual Average
| Chosen Level of Service: | 2026-27: No more than 3 in 100 Temporary Use Bans

## 1. BL Licences (hidden)
Table 1: Baseline licences |  |  |  |  | deployable output (Ml/d) |  |  | Licence Data | 1st line assurance
Row ref | Derivation | Licence number | Source name | Source type | Deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Constraints on deployable output
All individual licences:
0.1BL | Sum (0.1BL+...) | - | - | - | 31.9126 | 91.653 | -
- | Input |  |  |  | 0 | 8.51
- | Input |  |  |  | 0.0299 | 0.93
- | Input |  |  |  | 3.1779 | 4.558
- | Input |  |  |  | 1.2059 | 2.84
- | Input |  |  |  | 0.66 | 3.64
- | Input |  |  |  | 1.299 | 1.81
- | Input |  |  |  | 2.773 | 6.825
| Input |  |  |  | 5.024 | 8.75
| Input |  |  |  |  | 4.55
| Input |  |  |  | 2.6459 | 5.4
- | Input |  |  |  | 15.097 | 43.84
0.2BL | Sum (0.2BL+...) |  |  | - | 101.0445 | - | -
- | - |  |  | - | 35.419 | - | -
- | Input |  |  |  | 35.419 | 37 | .
- | Input
- | Input
- | - |  |  | - | 4.6469 | - | -
- | Input |  |  |  | 4.6469 | 5.498 | .
- | Input
- | Input
- | - |  |  | - | 11.7539 | - | -
- | Input |  |  |  | 11.7539 | 5.86 | .
- | Input |  |  |  |  | 5.67
- | Input |  |  |  |  | 6.82
- | - |  |  | - | 22.2549 | - | -
- | Input |  |  |  | 5.247 | 29.789 | .
- | Input
- | Input |  |  |  | 17.0079
- | Input
- | Input
- | - |  |  | - | 4.611 | - | -
- | Input |  |  |  | 4.611 | 2.27 | .
- | Input |  |  |  |  | 2.25
- | - |  |  | - | 22.3588 | - | -
- | Input |  |  |  | 8.2259 | 24.66 One Year / 23.01 FiveYear | .
- | Input |  |  |  | 0.619
- | Input |  |  |  | 13.5139
Unused licences: | Derivation |  |  | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Reason licence is unused
0.3BL | Sum (0.3BL+...) |  |  | - | 0 | 2.6086 | -
| Input |  |  |  | 0 | 1.6986 | .
- | Input |  |  |  | 0 | 0.91 | .
New licences (within current AMP): | Derivation |  |  | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Status of licence
0.4BL | Sum (0.4BL+...) |  |  | - | 0 | 0 | -
Input
- | Input
- | - |  |  | - | - | - | -
Company: |  | Severn Trent Water
Resource Zone Name: |  | North Staffordshire
Resource Zone Number: |  | 7
Planning Scenario Name: |  | Dry Year Annual Average
Chosen Level of Service: |  | No more than 3 in 100 Temporary Use Bans

## 2. BL Supply
Table 2: Baseline supply
| Row ref | Component | Derivation | Unit | decimal places | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| 1BL | Raw water abstracted | Input | Ml/d | 2 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629
Resources | 2BL | Total raw water imported | sum(2.1BL+2.2BL+2.3BL...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.1BL+ | Raw water imported from: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 |  | - | - | - | bar: 2021-22 to 2044-45
| 3BL | Total potable water imported | sum(3.1BL+3.2BL+3.3BL...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.1BL+ | Potable water imported from: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| 5BL | Total raw water exported (raw exports and non potable uses) | sum(5.1BL+5.2BL+...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.1BL | Non potable water supplied to: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.2BL+ | Raw water export to: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - |  | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| 6BL | Total potable water exported | sum(6.1BL+6.2BL+6.3BL...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.1BL+ | Potable water export to: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - |  | - | Ml/d | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| 7BL | Deployable Output (baseline profile without reductions) | sum(0.1Bl+0.2BL+0.3BL+0.4BL) | Ml/d | 2 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 132.9571
Resource (and process) Losses | 8BL | Baseline forecast changes to Deployable Output | sum(8.1BL+8.2BL+8.3BL) | Ml/d | 2 | 0 | 0 | 0 | 0 | -1.6 | -2 | -2.4 | -2.8 | -3.2 | -39.6 | -40 | -40.4 | -40.8 | -41.2 | -41.5 | -41.6 | -41.7 | -41.8 | -41.9 | -42 | -42.1 | -42.2 | -42.3 | -42.4 | -42.5 | -42.6 | -42.7 | -42.8 | -42.9
| 8.1BL | Change in DO due to climate change | Input (reductions must be expressed as -ve) | Ml/d | 2 | 0 | 0 | 0 | 0 | -1.6 | -2 | -2.4 | -2.8 | -3.2 | -3.6 | -4 | -4.4 | -4.8 | -5.2 | -5.5 | -5.6 | -5.7 | -5.8 | -5.9 | -6 | -6.1 | -6.2 | -6.3 | -6.4 | -6.5 | -6.6 | -6.7 | -6.8 | -6.9
| 8.2BL | Reductions to restore sustainable abstraction | sum(8.2BL sub components) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36
| 8.2BL+ | Modelled effect of WINEP3 | Input (zero or negative number) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36 | -36
| - | - | - | - | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.3BL | Total other changes to DO (specify, e.g. nitrates): None | Input (reductions must be expressed as -ve) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9BL | Raw water losses, treatment works losses and operational use | Input | Ml/d | 2 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039
| 10BL | Outage allowance | Input | Ml/d | 2 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69
|  | Company: | Severn Trent Water
|  | Resource Zone Name: | North Staffordshire
|  | Resource Zone Number: | 7
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans

## 3. BL Demand
Table 3: Baseline demand
| Row ref | Component | Derivation | Unit | Decimal places | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
Consumption | 19BL | Water delivered measured non-household | Input | Ml/d | 2 | 21.8159 | 21.8406 | 21.8257 | 21.8519 | 21.8324 | 21.9449 | 22.0173 | 22.0861 | 22.077 | 22.1599 | 22.179 | 22.1977 | 22.1565 | 22.233 | 22.2548 | 22.278 | 22.2394 | 22.3165 | 22.3311 | 22.345 | 22.2973 | 22.3736 | 22.3918 | 22.4109 | 22.3706 | 22.4517 | 22.4734 | 22.4957 | 22.4584
| 20BL | Water delivered unmeasured non- household | Input | Ml/d | 2 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738
| 21BL | Water delivered measured household | Input | Ml/d | 2 | 26.6642 | 27.4889 | 28.2978 | 29.1256 | 29.884 | 30.6629 | 31.45 | 32.2287 | 33.0097 | 33.7865 | 34.5566 | 35.3214 | 36.085 | 36.8369 | 37.4542 | 38.0697 | 38.6596 | 39.2373 | 39.799 | 40.3979 | 40.9907 | 41.5726 | 42.1379 | 42.6954 | 43.2416 | 43.7793 | 44.3106 | 44.832 | 45.3861
| 22BL | Water delivered unmeasured household | Input | Ml/d | 2 | 46.2133 | 45.2152 | 44.2273 | 43.2788 | 42.3167 | 41.4077 | 40.5316 | 39.679 | 38.8557 | 38.0535 | 37.2741 | 36.5143 | 35.7782 | 35.0561 | 34.3375 | 33.6263 | 32.9239 | 32.2385 | 31.5671 | 30.9375 | 30.3238 | 29.7232 | 29.1326 | 28.5558 | 27.9908 | 27.4376 | 26.8974 | 26.3683 | 25.8136
| 23BL | Measured Non Household - Consumption | 19BL-34BL | Ml/d | 2 | 21.386 | 21.4107 | 21.3958 | 21.422 | 21.4025 | 21.515 | 21.5873 | 21.6562 | 21.6471 | 21.7299 | 21.7491 | 21.7678 | 21.7266 | 21.8031 | 21.8249 | 21.8481 | 21.8095 | 21.8866 | 21.9012 | 21.9151 | 21.8674 | 21.9437 | 21.9619 | 21.981 | 21.9407 | 22.0217 | 22.0435 | 22.0658 | 22.0285
| 24BL | Unmeasured Non Household - Consumption | 20BL-35BL | Ml/d | 2 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433
| 25BL | Measured Household - Consumption | 21BL-36BL | Ml/d | 2 | 24.129 | 24.9018 | 25.6586 | 26.4346 | 27.1431 | 27.8733 | 28.6125 | 29.3442 | 30.0791 | 30.8108 | 31.5366 | 32.258 | 32.9791 | 33.6893 | 34.2657 | 34.8411 | 35.3916 | 35.9308 | 36.4546 | 37.0164 | 37.5728 | 38.1192 | 38.6495 | 39.1727 | 39.6853 | 40.1881 | 40.6852 | 41.173 | 41.6941
| 26BL | Unmeasured Household - Consumption | 22BL-37BL | Ml/d | 2 | 42.8391 | 41.9019 | 40.9749 | 40.0872 | 39.1836 | 38.332 | 37.5123 | 36.715 | 35.946 | 35.1971 | 34.4701 | 33.7617 | 33.0761 | 32.4035 | 31.7336 | 31.0702 | 30.4147 | 29.7754 | 29.1492 | 28.564 | 27.9939 | 27.4362 | 26.8876 | 26.3522 | 25.8278 | 25.3144 | 24.8133 | 24.3226 | 23.8057
| 27 - | Percentage of consumption driven by climate change | Input | % | 1 | 0 | 0.032311 | 0.064601 | 0.09687 | 0.12912 | 0.16135 | 0.19355 | 0.22574 | 0.2579 | 0.29005 | 0.32217 | 0.35428 | 0.38636 | 0.41842 | 0.45046 | 0.48248 | 0.51448 | 0.54646 | 0.57842 | 0.61036 | 0.64228 | 0.67417 | 0.70605 | 0.73791 | 0.76974 | 0.80156 | 0.83335 | 0.86513 | 0.89688
| 28 - | Volume of consumption driven by climate change |  | Ml/d | 1 | 0 | 0.028634 | 0.057129 | 0.085583 | 0.1138 | 0.14219 | 0.17055 | 0.19892 | 0.22715 | 0.25566 | 0.28403 | 0.31244 | 0.34071 | 0.36947 | 0.39744 | 0.42537 | 0.45285 | 0.48087 | 0.50849 | 0.5365 | 0.56417 | 0.59262 | 0.62064 | 0.6487 | 0.67628 | 0.7048 | 0.7329 | 0.76102 | 0.78865
PCC and consumption by component | 29BL | Measured Household - PCC | (25BL*1,000,000)/(51BL*1,000) | l/h/d | 1 | 112 | 111.5 | 111 | 110.7 | 110.3 | 110 | 109.8 | 109.7 | 109.5 | 109.5 | 109.5 | 109.5 | 109.5 | 109.6 | 109.3 | 109 | 108.8 | 108.5 | 108.3 | 108.2 | 108.1 | 108 | 107.9 | 107.8 | 107.7 | 107.6 | 107.6 | 107.5 | 107.4
| 29.1BL | Measured toilet flushing | Input | l/h/d | 1 | 25.4946 | 24.732 | 24.0154 | 23.3357 | 22.6896 | 22.071 | 21.4771 | 20.9063 | 20.3555 | 19.8243 | 19.3105 | 18.8124 | 18.3282 | 17.8576 | 17.832 | 17.8074 | 17.7841 | 17.7605 | 17.7372 | 17.7131 | 17.689 | 17.6644 | 17.6401 | 17.6151 | 17.5899 | 17.5645 | 17.5388 | 17.5129 | 17.4841
| 29.2BL | Measured personal washing | Input | l/h/d | 1 | 47.1755 | 47.9983 | 48.825 | 49.6522 | 50.4822 | 51.3113 | 52.1405 | 52.9692 | 53.7963 | 54.6261 | 55.4564 | 56.2882 | 57.1197 | 57.9547 | 57.9784 | 58.0061 | 58.0377 | 58.0683 | 58.0994 | 58.1277 | 58.1556 | 58.1821 | 58.2088 | 58.2335 | 58.2573 | 58.28 | 58.3019 | 58.3227 | 58.3336
| 29.3BL | Measured clothes washing | Input | l/h/d | 1 | 13.9195 | 13.8272 | 13.7401 | 13.6564 | 13.5759 | 13.4973 | 13.4207 | 13.3459 | 13.2726 | 13.2015 | 13.132 | 13.0642 | 12.9975 | 12.9327 | 12.8339 | 12.7359 | 12.6386 | 12.5411 | 12.4435 | 12.3453 | 12.2469 | 12.1482 | 12.0494 | 11.9501 | 11.8505 | 11.7507 | 11.6506 | 11.5502 | 11.4479
| 29.4BL | Measured dish washing | Input | l/h/d | 1 | 10.9572 | 10.9519 | 10.9479 | 10.9442 | 10.9413 | 10.9383 | 10.9354 | 10.9326 | 10.9295 | 10.9271 | 10.9249 | 10.923 | 10.9211 | 10.9199 | 10.9152 | 10.9112 | 10.908 | 10.9046 | 10.9013 | 10.8975 | 10.8936 | 10.8894 | 10.8853 | 10.8807 | 10.8761 | 10.8712 | 10.8661 | 10.8608 | 10.8537
| 29.5BL | Measured miscellaneous internal use | Input | l/h/d | 1 | 13.1684 | 13.0812 | 13.0033 | 12.932 | 12.8676 | 12.8079 | 12.7522 | 12.7007 | 12.6525 | 12.6082 | 12.5674 | 12.5296 | 12.4944 | 12.4624 | 12.431 | 12.4011 | 12.3737 | 12.3479 | 12.3236 | 12.3003 | 12.2781 | 12.2568 | 12.2368 | 12.2174 | 12.1988 | 12.181 | 12.1638 | 12.1473 | 12.1294
| 29.6BL | Measured external use | Input | l/h/d | 1 | 1.3034 | 1.3402 | 1.3769 | 1.4135 | 1.4498 | 1.486 | 1.522 | 1.5579 | 1.5938 | 1.6297 | 1.6657 | 1.7017 | 1.7377 | 1.7739 | 1.8081 | 1.842 | 1.8755 | 1.9087 | 1.9415 | 1.9741 | 2.0063 | 2.0383 | 2.0699 | 2.1013 | 2.1324 | 2.1631 | 2.1936 | 2.2238 | 2.2542
| 29.7BL | Measured water efficiency savings | Input | l/h/d | 1 | -0.018667 | -0.43075 | -0.90852 | -1.234 | -1.7064 | -2.1116 | -2.4478 | -2.7126 | -3.1003 | -3.317 | -3.5568 | -3.8191 | -4.0986 | -4.3012 | -4.4986 | -4.7037 | -4.8176 | -5.031 | -5.1466 | -5.158 | -5.1695 | -5.1793 | -5.1902 | -5.1982 | -5.205 | -5.2104 | -5.1149 | -5.1177 | -5.1029
| 30BL | Unmeasured Household - PCC | (26BL*1,000,000)/(52BL*1,000) | l/h/d | 1 | 138.4 | 138.1 | 137.8 | 137.5 | 137.2 | 136.9 | 136.7 | 136.4 | 136.2 | 136 | 135.8 | 135.6 | 135.4 | 135.2 | 135 | 134.8 | 134.6 | 134.4 | 134.3 | 134.2 | 134.2 | 134.2 | 134.2 | 134.1 | 134.1 | 134 | 134 | 134 | 134.1
| 30.1BL | Unmeasured toilet flushing | Input | l/h/d | 1 | 31.2067 | 30.4165 | 29.6282 | 28.8375 | 28.0494 | 27.2579 | 26.4648 | 25.6689 | 24.8695 | 24.0711 | 23.2711 | 22.4707 | 21.6682 | 20.867 | 20.8379 | 20.8134 | 20.7925 | 20.7716 | 20.7516 | 20.7299 | 20.7085 | 20.6866 | 20.6656 | 20.6434 | 20.6211 | 20.5986 | 20.576 | 20.5531 | 20.5494
| 30.2BL | Unmeasured personal washing | Input | l/h/d | 1 | 57.8437 | 58.7166 | 59.596 | 60.4732 | 61.359 | 62.2405 | 63.1212 | 63.9982 | 64.8687 | 65.7441 | 66.6177 | 67.4926 | 68.3635 | 69.2409 | 69.2587 | 69.2917 | 69.3371 | 69.3821 | 69.4307 | 69.4739 | 69.518 | 69.5606 | 69.6062 | 69.6482 | 69.69 | 69.7309 | 69.772 | 69.8121 | 69.9175
| 30.3BL | Unmeasured clothes washing | Input | l/h/d | 1 | 16.6882 | 16.5959 | 16.5051 | 16.4133 | 16.3234 | 16.232 | 16.14 | 16.0468 | 15.9517 | 15.8575 | 15.7627 | 15.6679 | 15.572 | 15.4774 | 15.3574 | 15.2406 | 15.1265 | 15.0121 | 14.8983 | 14.7832 | 14.6682 | 14.5527 | 14.4376 | 14.3216 | 14.2055 | 14.089 | 13.9724 | 13.8554 | 13.7512
| 30.4BL | Unmeasured dish washing | Input | l/h/d | 1 | 13.1993 | 13.1956 | 13.1932 | 13.19 | 13.1885 | 13.1859 | 13.1828 | 13.1788 | 13.1733 | 13.1687 | 13.1636 | 13.1585 | 13.1526 | 13.1478 | 13.141 | 13.137 | 13.1354 | 13.1338 | 13.1327 | 13.1307 | 13.1288 | 13.1266 | 13.1249 | 13.1226 | 13.1202 | 13.1177 | 13.1151 | 13.1124 | 13.1219
| 30.5BL | Unmeasured miscellaneous internal use | Input | l/h/d | 1 | 18.0701 | 18.0789 | 18.0895 | 18.0991 | 18.1109 | 18.1212 | 18.131 | 18.1395 | 18.1459 | 18.1536 | 18.1605 | 18.1677 | 18.1735 | 18.181 | 18.1856 | 18.1943 | 18.2062 | 18.2181 | 18.2308 | 18.2421 | 18.2537 | 18.2649 | 18.2769 | 18.2879 | 18.2989 | 18.3096 | 18.3204 | 18.331 | 18.3586
| 30.6BL | Unmeasured external use | Input | l/h/d | 1 | 1.4393 | 1.4847 | 1.5302 | 1.5755 | 1.621 | 1.6662 | 1.7114 | 1.7564 | 1.8012 | 1.846 | 1.8907 | 1.9353 | 1.9798 | 2.0243 | 2.0682 | 2.1121 | 2.1562 | 2.2001 | 2.2439 | 2.2874 | 2.3309 | 2.3742 | 2.4173 | 2.4603 | 2.5031 | 2.5458 | 2.5883 | 2.6307 | 2.6736
| 30.7BL | Unmeasured water efficiency savings | Input | l/h/d | 1 | -0.047295 | -0.38824 | -0.74221 | -1.0886 | -1.4522 | -1.8038 | -2.0513 | -2.3887 | -2.6102 | -2.8408 | -3.0663 | -3.2928 | -3.5097 | -3.7384 | -3.8488 | -3.9893 | -4.154 | -4.3177 | -4.388 | -4.4473 | -4.4081 | -4.3655 | -4.3284 | -4.3841 | -4.3388 | -4.3915 | -4.3442 | -4.2947 | -4.2723
| 31BL | Average Household - PCC | ((25BL+26BL)*1,000,000))/(51BL+52BL*1,000) | l/h/d | 1 | 127.6004 | 126.8047 | 126.0791 | 125.4797 | 124.756 | 124.1492 | 123.6063 | 123.0846 | 122.5969 | 122.1673 | 121.7759 | 121.4236 | 121.1084 | 120.8349 | 120.3156 | 119.8242 | 119.3609 | 118.9109 | 118.4774 | 118.1686 | 117.8846 | 117.6027 | 117.3251 | 117.0479 | 116.7739 | 116.5025 | 116.2469 | 115.993 | 115.7528
| 32BL | Water Taken Unbilled | Input | Ml/d | 2 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134
| 33BL | Distribution System Operational Use | Input | Ml/d | 2 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721
Leakage | 34BL | Measured Non Household - USPL | Input | Ml/d | 2 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992
| 35BL | Unmeasured Non Household - USPL | Input | Ml/d | 2 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305
| 36BL | Measured Household - USPL | Input | Ml/d | 2 | 2.5352 | 2.5872 | 2.6391 | 2.6911 | 2.7409 | 2.7897 | 2.8375 | 2.8845 | 2.9305 | 2.9757 | 3.0199 | 3.0633 | 3.1059 | 3.1476 | 3.1885 | 3.2286 | 3.268 | 3.3066 | 3.3444 | 3.3815 | 3.4178 | 3.4535 | 3.4884 | 3.5227 | 3.5563 | 3.5911 | 3.6254 | 3.659 | 3.692
| 37BL | Unmeasured Household - USPL | Input | Ml/d | 2 | 3.3742 | 3.3133 | 3.2524 | 3.1915 | 3.1331 | 3.0757 | 3.0193 | 2.964 | 2.9097 | 2.8564 | 2.804 | 2.7526 | 2.7021 | 2.6526 | 2.6039 | 2.5561 | 2.5092 | 2.4631 | 2.4179 | 2.3735 | 2.3299 | 2.287 | 2.245 | 2.2036 | 2.1631 | 2.1232 | 2.0841 | 2.0457 | 2.0079
| 38BL | Void Properties - USPL | Input | Ml/d | 2 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992
| 39BL | Distribution Losses | Input | Ml/d | 2 | 23.0777 | 22.9367 | 22.7956 | 22.6545 | 22.6632 | 22.6718 | 22.6802 | 22.6886 | 22.6969 | 22.705 | 22.7131 | 22.7212 | 22.7291 | 22.7369 | 22.7447 | 22.7523 | 22.7599 | 22.7674 | 22.7748 | 22.7822 | 22.7894 | 22.7966 | 22.8037 | 22.8108 | 22.8178 | 22.8227 | 22.8276 | 22.8324 | 22.8371
| 40BL | Total Leakage | sum(34BL:39BL) | Ml/d | 2 | 29.86 | 29.71 | 29.56 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41 | 29.41
| 41BL | Total Leakage | (40BL*1,000,000)/(48BL*1,000) | l/prop/d | 2 | 118.9865 | 117.5697 | 116.1995 | 114.8597 | 114.1149 | 113.3766 | 112.6376 | 111.9142 | 111.2018 | 110.4984 | 109.8144 | 109.1424 | 108.4873 | 107.8458 | 107.2374 | 106.5937 | 105.9577 | 105.3292 | 104.7081 | 104.0943 | 103.4865 | 102.8858 | 102.292 | 101.7051 | 101.1248 | 100.5511 | 99.9839 | 99.4231 | 98.8685
Customer: Properties | 42BL | Measured non-households - properties | Input (total, excluding voids) | 000's | 2 | 11.7713 | 11.8173 | 11.8633 | 11.9093 | 11.9553 | 12.0013 | 12.0473 | 12.0933 | 12.1393 | 12.1853 | 12.2313 | 12.2773 | 12.3233 | 12.3692 | 12.4152 | 12.4612 | 12.5071 | 12.5531 | 12.599 | 12.645 | 12.6909 | 12.7368 | 12.7828 | 12.8287 | 12.8746 | 12.9205 | 12.9664 | 13.0124 | 13.0583
| 43BL | Unmeasured non-households - properties | Input (total, excluding voids) | 000's | 2 | 0.49182 | 0.48371 | 0.47559 | 0.46747 | 0.45936 | 0.45124 | 0.44312 | 0.43501 | 0.42689 | 0.41877 | 0.41066 | 0.40254 | 0.39442 | 0.38631 | 0.37819 | 0.37007 | 0.36195 | 0.35384 | 0.34572 | 0.3376 | 0.32949 | 0.32137 | 0.31325 | 0.30514 | 0.29702 | 0.2889 | 0.28079 | 0.27267 | 0.26455
| 44BL | All void non-households - properties | Input (voids in each year) | 000's | 2 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993
| 45BL | Total measured households - properties (excl void) | Pre-plan year = input. Forecast years = Previous year 45BL + sum(45.1BL:45.6BL) | 000's | 2 | 98.3805 | 102.3525 | 106.2614 | 110.1396 | 113.9363 | 117.6986 | 121.4433 | 125.1341 | 128.7816 | 132.3908 | 135.9364 | 139.4366 | 142.879 | 146.2716 | 149.5643 | 152.932 | 156.2666 | 159.5687 | 162.8389 | 166.0779 | 169.2894 | 172.4709 | 175.6231 | 178.7465 | 181.8417 | 184.9094 | 187.9499 | 190.9639 | 193.9518
| 45.1BL | New build properties - properties | Input (new builds in each year) | 000's | 2 | 1.8356 | 1.8316 | 1.77 | 1.7409 | 1.7487 | 1.7543 | 1.7758 | 1.7601 | 1.7544 | 1.7528 | 1.7254 | 1.7152 | 1.692 | 1.6761 | 1.6096 | 1.7168 | 1.7154 | 1.7141 | 1.7127 | 1.7115 | 1.7133 | 1.712 | 1.7108 | 1.7096 | 1.7085 | 1.7073 | 1.7062 | 1.7051 | 1.7041
| 45.2BL | Meter optants - properties | Input (meter optants in each year) | 000's | 2 | 2.245 | 2.1921 | 2.1897 | 2.1874 | 2.0973 | 2.0565 | 2.0167 | 1.9777 | 1.9395 | 1.902 | 1.8653 | 1.8294 | 1.7942 | 1.7598 | 1.7259 | 1.6929 | 1.6606 | 1.6288 | 1.5977 | 1.5673 | 1.5374 | 1.5081 | 1.4795 | 1.4514 | 1.4239 | 1.3969 | 1.3705 | 1.3445 | 1.3191
| 45.3BL | Compulsory metering - properties | Input (compulsory meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.4BL | Metering on change of occupancy - properties | Input (change of occupancy meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.5BL | Selective metering - properties | Input (selective meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.6BL | Other changes to existing metering - properties | Input (other changes to meters in each year) | 000's | 2 | 0 | -0.051627 | -0.050818 | -0.050047 | -0.049278 | -0.048523 | -0.04776 | -0.047055 | -0.046358 | -0.045671 | -0.045052 | -0.044423 | -0.043842 | -0.043268 | -0.042848 | -0.041979 | -0.041397 | -0.040826 | -0.040266 | -0.039719 | -0.039171 | -0.038645 | -0.038129 | -0.037623 | -0.037127 | -0.036641 | -0.036164 | -0.035697 | -0.035239
| 45.7BL | Measured void households - properties | Input (voids in each year) | 000's | 2 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217
| 46BL | Unmeasured households - properties (excl void) | Input (total) | 000's | 2 | 124.4512 | 122.1898 | 119.9318 | 117.6771 | 115.5136 | 113.3919 | 111.311 | 109.2701 | 107.2684 | 105.305 | 103.3792 | 101.4901 | 99.6369 | 97.819 | 96.0355 | 94.2862 | 92.57 | 90.8863 | 89.2345 | 87.6139 | 86.0238 | 84.4638 | 82.933 | 81.4311 | 79.9573 | 78.5112 | 77.0921 | 75.6996 | 74.3331
| 47BL | Unmeasured void households - properties | Input (voids in each year) | 000's | 2 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369
| 48BL | Total Resource Zone Properties (incl voids) | SUM(42BL:45BL)+45.7BL+46BL+47BL | 000's | 2 | 250.9527 | 252.7012 | 254.3901 | 256.0515 | 257.7226 | 259.401 | 261.1028 | 262.7905 | 264.4742 | 266.1578 | 267.8155 | 269.4645 | 271.0916 | 272.7041 | 274.2512 | 275.9074 | 277.5637 | 279.2199 | 280.8761 | 282.5323 | 284.1916 | 285.8509 | 287.5101 | 289.1694 | 290.8287 | 292.488 | 294.1472 | 295.8065 | 297.4657
Customer: Population | 49BL | Measured Non Household - Population | Input (total) | 000's | 2 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064
| 50BL | Unmeasured Non Household - Population | Input (total) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 51BL | Measured Household - Population | Input (total) | 000's | 2 | 215.4017 | 223.382 | 231.0953 | 238.698 | 246.026 | 253.2826 | 260.4756 | 267.5523 | 274.5708 | 281.4238 | 288.1251 | 294.6861 | 301.1368 | 307.3825 | 313.4883 | 319.5622 | 325.3862 | 331.104 | 336.6723 | 342.2011 | 347.6229 | 352.9647 | 358.1715 | 363.3289 | 368.3981 | 373.3889 | 378.2909 | 383.1202 | 388.3032
| 52BL | Unmeasured Household - Population | Input (total) | 000's | 2 | 309.4255 | 303.4415 | 297.4106 | 291.4419 | 285.6263 | 279.9895 | 274.4872 | 269.1448 | 263.9842 | 258.884 | 253.9089 | 249.0278 | 244.2852 | 239.585 | 235.063 | 230.504 | 225.9359 | 221.4625 | 217.0521 | 212.7725 | 208.5715 | 204.4665 | 200.4222 | 196.4842 | 192.6269 | 188.8522 | 185.1518 | 181.531 | 177.5557
| 53BL | Total Resource Zone Population | Sum(49BL:52BL) | 000's | 2 | 534.8912 | 536.8875 | 538.5699 | 540.2038 | 541.7162 | 543.3361 | 545.0268 | 546.7611 | 548.619 | 550.3718 | 552.098 | 553.7779 | 555.486 | 557.0315 | 558.6154 | 560.1302 | 561.386 | 562.6305 | 563.7884 | 565.0376 | 566.2584 | 567.4952 | 568.6577 | 569.8771 | 571.089 | 572.3051 | 573.5067 | 574.7151 | 575.9228
Occupancy | 54BL | Measured Household - Occupancy Rate (average) (excl voids) | 51BL/45BL | h/prop | 1 | 2.1895 | 2.1825 | 2.1748 | 2.1672 | 2.1593 | 2.152 | 2.1448 | 2.1381 | 2.1321 | 2.1257 | 2.1196 | 2.1134 | 2.1076 | 2.1015 | 2.096 | 2.0896 | 2.0823 | 2.075 | 2.0675 | 2.0605 | 2.0534 | 2.0465 | 2.0394 | 2.0326 | 2.0259 | 2.0193 | 2.0127 | 2.0062 | 2.0021
| 55BL | Unmeasured Household - Occupancy Rate | 52BL/46BL | h/prop | 1 | 2.4863 | 2.4834 | 2.4798 | 2.4766 | 2.4727 | 2.4692 | 2.4659 | 2.4631 | 2.461 | 2.4584 | 2.4561 | 2.4537 | 2.4518 | 2.4493 | 2.4477 | 2.4447 | 2.4407 | 2.4367 | 2.4324 | 2.4285 | 2.4246 | 2.4208 | 2.4167 | 2.4129 | 2.4091 | 2.4054 | 2.4017 | 2.398 | 2.3886
Metering | 56BL | Total Household Metering penetration (excl. voids) | 45BL/45BL+46BL | % | 0 | 44.15% | 45.58% | 46.98% | 48.35% | 49.66% | 50.93% | 52.18% | 53.38% | 54.56% | 55.7% | 56.8% | 57.88% | 58.92% | 59.93% | 60.9% | 61.86% | 62.8% | 63.71% | 64.6% | 65.46% | 66.31% | 67.13% | 67.92% | 68.7% | 69.46% | 70.2% | 70.91% | 71.61% | 72.29%
| 57BL | Total Household Metering penetration (incl. voids) | 45BL/(45BL+45.7BL+46BL+47BL) | % | 0 | 41.83% | 43.2% | 44.54% | 45.86% | 47.12% | 48.35% | 49.55% | 50.71% | 51.84% | 52.94% | 54.01% | 55.05% | 56.06% | 57.04% | 57.98% | 58.92% | 59.83% | 60.72% | 61.58% | 62.42% | 63.25% | 64.05% | 64.83% | 65.59% | 66.33% | 67.05% | 67.75% | 68.44% | 69.11%
|  | Company: | Severn Trent Water
|  | Resource Zone Name: | North Staffordshire
|  | Resource Zone Number: | 7
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans

## 4. BL SDB
Table 4: Baseline supply demand balance
| Row ref | Component | Derivation | Unit | Decimal places | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
SDB | 11BL | Distribution input | 19BL+20BL+21BL+22BL+32BL+33BL+38BL+39BL | Ml/d | 2 | 122.2691 | 121.9794 | 121.6443 | 121.4087 | 121.1942 | 121.1853 | 121.1771 | 121.1803 | 121.1372 | 121.2029 | 121.2208 | 121.2524 | 121.2468 | 121.3608 | 121.2892 | 121.2243 | 121.0808 | 121.0577 | 120.97 | 120.9605 | 120.8991 | 120.964 | 120.964 | 120.9709 | 120.9187 | 120.9892 | 121.0069 | 121.0263 | 120.9932
| 12BL | Water Available For Use (own sources) | (7BL+8BL)-(10BL) | Ml/d | 2 | 131.2671 | 131.2671 | 131.2671 | 131.2671 | 129.6671 | 129.2671 | 128.8671 | 128.4671 | 128.0671 | 91.6671 | 91.2671 | 90.8671 | 90.4671 | 90.0671 | 89.7671 | 89.6671 | 89.5671 | 89.4671 | 89.3671 | 89.2671 | 89.1671 | 89.0671 | 88.9671 | 88.8671 | 88.7671 | 88.6671 | 88.5671 | 88.4671 | 88.3671
| 13BL | Total Water Available For Use | 12BL+(2BL+3BL)-(5BL+6BL) | Ml/d | 2 | 131.2671 | 131.2671 | 131.2671 | 131.2671 | 129.6671 | 129.2671 | 128.8671 | 128.4671 | 128.0671 | 91.6671 | 91.2671 | 90.8671 | 90.4671 | 90.0671 | 89.7671 | 89.6671 | 89.5671 | 89.4671 | 89.3671 | 89.2671 | 89.1671 | 89.0671 | 88.9671 | 88.8671 | 88.7671 | 88.6671 | 88.5671 | 88.4671 | 88.3671
| 14BL | Target headroom (climate change component) | Input | Ml/d | 2 | 0 | 0.24775 | 0.48499 | 0.7085 | 0.96641 | 1.162 | 1.3439 | 1.6498 | 1.8938 | 1.9159 | 2.1404 | 2.4168 | 2.6475 | 2.9631 | 3.1278 | 3.1258 | 3.2322 | 3.3224 | 3.283 | 3.3923 | 3.4104 | 3.5045 | 3.6565 | 3.6711 | 3.7877 | 4.0262 | 4.25 | 4.5035 | 4.8624
| 15BL | Target headroom (All other components) | Input | Ml/d | 2 | 4.4322 | 4.2288 | 3.9968 | 3.8487 | 3.798 | 3.6527 | 3.5209 | 3.7092 | 3.6483 | 2.8405 | 2.8719 | 3.013 | 3.0031 | 3.1805 | 3.3254 | 3.2621 | 3.342 | 3.277 | 3.3661 | 3.3389 | 3.3704 | 3.5033 | 3.6337 | 3.6186 | 3.6883 | 3.7835 | 3.8788 | 4.0863 | 4.3155
| 16BL | Target Headroom | 14BL+15BL | Ml/d | 2 | 4.4322 | 4.4766 | 4.4817 | 4.5572 | 4.7644 | 4.8147 | 4.8648 | 5.3589 | 5.5421 | 4.7564 | 5.0122 | 5.4298 | 5.6506 | 6.1436 | 6.4532 | 6.3879 | 6.5742 | 6.5994 | 6.6491 | 6.7311 | 6.7808 | 7.0079 | 7.2902 | 7.2897 | 7.476 | 7.8097 | 8.1288 | 8.5897 | 9.1779
| 17BL | Available Headroom | 13BL-11BL | Ml/d | 2 | 8.998 | 9.2877 | 9.6228 | 9.8584 | 8.4729 | 8.0818 | 7.69 | 7.2868 | 6.9299 | -29.5358 | -29.9537 | -30.3853 | -30.7797 | -31.2937 | -31.5221 | -31.5572 | -31.5137 | -31.5906 | -31.6029 | -31.6934 | -31.732 | -31.8969 | -31.9969 | -32.1038 | -32.1516 | -32.3221 | -32.4398 | -32.5592 | -32.6261
| 18BL | Supply Demand Balance | 17BL-16BL | Ml/d | 2 | 4.5658 | 4.8112 | 5.1411 | 5.3011 | 3.7085 | 3.2672 | 2.8252 | 1.9279 | 1.3878 | -34.2922 | -34.9659 | -35.8151 | -36.4303 | -37.4373 | -37.9753 | -37.945 | -38.0879 | -38.1901 | -38.252 | -38.4245 | -38.5128 | -38.9048 | -39.2871 | -39.3936 | -39.6276 | -40.1317 | -40.5686 | -41.149 | -41.804
|  | Company: | Severn Trent Water
|  | Resource Zone Name: | North Staffordshire
|  | Resource Zone Number: | 7
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans

## 5. Feasible Options
Table 5: Feasible options detailed costs | [18 empty] | ENTER DISCOUNT RATE % |  |  |  | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
Detail the gains in WAFU / savings in demand, and the costs of feasible options under capacity use scenario | [18 empty] | ENTER DISCOUNT PERIOD (YRS) | 80 |  | 1 | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35801 | 0.34758 | 0.33746 | 0.32763 | 0.31809 | 0.30882 | 0.29983 | 0.29109 | 0.28261 | 0.27438 | 0.26639 | 0.25863 | 0.2511 | 0.24379 | 0.23669 | 0.22979 | 0.2231 | 0.2166 | 0.21029 | 0.20417 | 0.19822 | 0.19245 | 0.18684 | 0.1814 | 0.17612 | 0.17099 | 0.16601 | 0.16117 | 0.15648 | 0.15192 | 0.14749 | 0.1432 | 0.13903 | 0.13498 | 0.13105 | 0.12723 | 0.12352 | 0.11993 | 0.11643 | 0.11304 | 0.10975 | 0.10655 | 0.10345 | 0.10044 | 0.097511 | 0.095133 | 0.092813 | 0.090549 | 0.08834 | 0.086186 | Note: If option costs are required from beyond year 80 then the NPV calculation formula must be amended manually to cover the extended period
[22 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104
Row ref | Option name | Option reference no. | Type of option | Preferred Option (Y/N) | Earliest potential option start date (Year) | Costs based on capacity | WAFU on full implementation (Ml/d) | NPV of WAFU (Ml) | CAPEX NPV (£000) | OPEX NPV (£000) | NPV of opex savings (£000) | NPV of carbon (£000) | Social & Env. NPV (£000) | TOTAL NPV (£000) | AIC (p/m3) | AISC (p/m3) | Scope confidence (score 1 to 5) | Cost confidence (score 1 to 5) | Cost component | Derivation | Unit | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50 | Year 51 | Year 52 | Year 53 | Year 54 | Year 55 | Year 56 | Year 57 | Year 58 | Year 59 | Year 60 | Year 61 | Year 62 | Year 63 | Year 64 | Year 65 | Year 66 | Year 67 | Year 68 | Year 69 | Year 70 | Year 71 | Year 72 | Year 73 | Year 74 | Year 75 | Year 76 | Year 77 | Year 78 | Year 79 | Year 80 | Year 81 | Year 82 | Year 83 | Year 84 | Year 85 | Year 86 | Year 87 | Year 88 | Year 89 | Year 90 | Year 91 | Year 92 | Year 93 | Year 94 | Year 95 | Year 96 | Year 97 | Year 98 | Year 99 | Year 100 | Year 101 | Year 102 | Year 103 | Year 104
58a | RESOURCE SIDE | bar: 1 Year 1 to 80 Year 80
58.1a | Options to increase raw water abstractions | [17 empty] | Total Mld for SDB component |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Swynnerton BHs asset and water treatment enhancements | BHS04 | GW enhancement | N | 2025-26 | Capacity | 7 | 60954.4775 | 29411.3061 | 9523.7407 | 0 | 577.3169 | 52.0286 | 39564.3923 | 63.8756 | 64.9081 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 1517.67 | 1734.48 | 2168.1 | 8672.4 | 7588.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.16 | 783.04 | 978.8 | 3915.2 | 3425.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.16 | 783.04 | 978.8 | 3915.2 | 3425.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1499.82 | 1714.08 | 2142.6 | 8570.4 | 7499.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 365.8021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.2842 | 0.3248 | 0.406 | 1.624 | 1.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1283 | 0.14663 | 0.18329 | 0.73316 | 0.64152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1283 | 0.14663 | 0.18329 | 0.73316 | 0.64152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28086 | 0.32098 | 0.40122 | 1.6049 | 1.4043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 2.2868 | 2.6135 | 3.2669 | 13.0677 | 11.4342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0324 | 1.1799 | 1.4749 | 5.8995 | 5.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0324 | 1.1799 | 1.4749 | 5.8995 | 5.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2599 | 2.5828 | 3.2285 | 12.914 | 11.2997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 59.1125 | 54.7599 | 52.0471 | 51.1227 | 47.6388 | 44.9707 | 42.3026 | 39.6344 | 36.9663 | 34.2982 | 31.6301 | 28.962 | 26.2938 | 23.6257 | 20.9576 | 18.2895 | 15.6214 | 12.9532 | 10.2851 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 7.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1520.241 | 1737.4183 | 2171.7729 | 8687.0917 | 7601.2052 | 460.2647 | 455.9121 | 453.1992 | 452.2749 | 448.7909 | 446.1228 | 443.4547 | 440.7866 | 438.1185 | 435.4503 | 432.7822 | 430.1141 | 427.446 | 424.7779 | 422.1097 | 1105.7623 | 1201.14 | 1394.5635 | 4333.2699 | 3840.3727 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 1095.0898 | 1193.1357 | 1389.2273 | 4330.6018 | 3840.3727 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 1911.1299 | 2125.7529 | 2554.9989 | 8993.688 | 7920.5732 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 408.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Elmhurst BH asset and water treatment enhancements | BHS09 | GW enhancement | N | 2025-26 | Capacity | 2 | 17415.565 | 23297.2792 | 3797.4997 | 0 | 202.4218 | 23.2039 | 27320.4047 | 155.5779 | 156.8735 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 1304.17 | 1490.48 | 1863.1 | 7452.4 | 6520.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 446.88 | 510.72 | 638.4 | 2553.6 | 2234.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 446.88 | 510.72 | 638.4 | 2553.6 | 2234.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.21 | 1144.24 | 1430.3 | 5721.2 | 5006.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 115.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.511 | 0.584 | 0.73 | 2.92 | 2.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1751 | 0.20011 | 0.25014 | 1.0006 | 0.87548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1751 | 0.20011 | 0.25014 | 1.0006 | 0.87548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39229 | 0.44834 | 0.56042 | 2.2417 | 1.9615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 3.618 | 4.1348 | 5.1686 | 20.6742 | 18.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2397 | 1.4168 | 1.771 | 7.0841 | 6.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2397 | 1.4168 | 1.771 | 7.0841 | 6.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7775 | 3.1743 | 3.9679 | 15.8716 | 13.8876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 15.2818 | 14.1565 | 13.4552 | 13.2163 | 12.3156 | 11.6258 | 10.9361 | 10.2463 | 9.5565 | 8.8668 | 8.177 | 7.4873 | 6.7975 | 6.1077 | 5.418 | 4.7282 | 4.0384 | 3.3487 | 2.6589 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 1.9691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1308.299 | 1495.1988 | 1868.9986 | 7475.9942 | 6541.495 | 175.0498 | 173.9245 | 173.2232 | 172.9843 | 172.0836 | 171.3938 | 170.7041 | 170.0143 | 169.3245 | 168.6348 | 167.945 | 167.2553 | 166.5655 | 165.8757 | 165.186 | 612.791 | 676.1434 | 803.5378 | 2724.1116 | 2403.2112 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 610.032 | 674.0741 | 802.1583 | 2723.4218 | 2403.2112 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 1166.117 | 1309.5998 | 1596.5655 | 5901.0504 | 5183.6363 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 161.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Elmhurst BH asset enhancements and transfer to Site L | BHS10 | GW enhancement | N | 2025-26 | Capacity | 2 | 17415.565 | 8856.0579 | 2483.5073 | 0 | 224.0376 | 26.256 | 11589.8587 | 65.1117 | 66.5489 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 595.7 | 680.8 | 851 | 3404 | 2978.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.51 | 71.44 | 89.3 | 357.2 | 312.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.51 | 71.44 | 89.3 | 357.2 | 312.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266.98 | 305.12 | 381.4 | 1525.6 | 1334.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.2737 | 0.3128 | 0.391 | 1.564 | 1.3685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028721 | 0.032824 | 0.04103 | 0.16412 | 0.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028721 | 0.032824 | 0.04103 | 0.16412 | 0.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12267 | 0.14019 | 0.17524 | 0.70095 | 0.61333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 5.6659 | 6.4753 | 8.0942 | 32.3766 | 28.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59455 | 0.67949 | 0.84936 | 3.3975 | 2.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59455 | 0.67949 | 0.84936 | 3.3975 | 2.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5393 | 2.9021 | 3.6276 | 14.5105 | 12.6967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 15.5051 | 14.3634 | 13.6518 | 13.4094 | 12.4955 | 11.7957 | 11.0959 | 10.396 | 9.6962 | 8.9963 | 8.2965 | 7.5967 | 6.8968 | 6.197 | 5.4971 | 4.7973 | 4.0974 | 3.3976 | 2.6978 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 1.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 601.6396 | 687.5881 | 859.4852 | 3437.9406 | 3008.1981 | 120.5351 | 119.3934 | 118.6818 | 118.4394 | 117.5255 | 116.8257 | 116.1259 | 115.426 | 114.7262 | 114.0263 | 113.3265 | 112.6267 | 111.9268 | 111.227 | 110.5271 | 172.9606 | 181.2798 | 198.618 | 468.4893 | 422.6943 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 170.1612 | 179.1802 | 197.2183 | 467.7895 | 422.6943 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 376.6699 | 415.1902 | 492.2308 | 1647.8394 | 1455.238 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 107.0279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Croxton BH output increase and transfer to Hob Hill DSR | BHS13 | GW enhancement | N | 2025-26 | Capacity | 2.5 | 21769.4563 | 23039.1043 | 3807.5597 | 0 | 181.9233 | 16.514 | 27045.1014 | 123.3226 | 124.2342 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 1261.4 | 1441.6 | 1802 | 7208 | 6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469.21 | 536.24 | 670.3 | 2681.2 | 2346.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469.21 | 536.24 | 670.3 | 2681.2 | 2346.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038.52 | 1186.88 | 1483.6 | 5934.4 | 5192.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 118.8997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.238 | 0.272 | 0.34 | 1.36 | 1.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08853 | 0.10118 | 0.12647 | 0.50589 | 0.44265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08853 | 0.10118 | 0.12647 | 0.50589 | 0.44265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19595 | 0.22394 | 0.27992 | 1.1197 | 0.97974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 1.9797 | 2.2625 | 2.8281 | 11.3123 | 9.8983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73638 | 0.84158 | 1.052 | 4.2079 | 3.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73638 | 0.84158 | 1.052 | 4.2079 | 3.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6299 | 1.8627 | 2.3284 | 9.3135 | 8.1493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 16.1662 | 14.9758 | 14.2339 | 13.9811 | 13.0283 | 12.2986 | 11.569 | 10.8393 | 10.1096 | 9.3799 | 8.6502 | 7.9206 | 7.1909 | 6.4612 | 5.7315 | 5.0018 | 4.2722 | 3.5425 | 2.8128 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 2.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1263.6177 | 1444.1345 | 1805.1681 | 7220.6723 | 6318.0883 | 176.2759 | 175.0855 | 174.3436 | 174.0908 | 173.138 | 172.4083 | 171.6786 | 170.949 | 170.2193 | 169.4896 | 168.7599 | 168.0302 | 167.3006 | 166.5709 | 165.8412 | 635.1464 | 701.5646 | 835.1306 | 2848.8363 | 2512.3674 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 632.2277 | 699.3755 | 833.6712 | 2848.1066 | 2512.3674 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 1202.5386 | 1351.1594 | 1648.4011 | 6107.026 | 5363.9219 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 162.1928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Croxton BH output increase and transfer to Hanchurch DSR | BHS14 | GW enhancement | N | 2025-26 | Capacity | 2.5 | 21769.4563 | 25218.4911 | 4882.2728 | 0 | 277.8712 | 22.0663 | 30400.7015 | 138.2706 | 139.6484 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 1401.12 | 1601.28 | 2001.6 | 8006.4 | 7005.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495.18 | 565.92 | 707.4 | 2829.6 | 2475.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495.18 | 565.92 | 707.4 | 2829.6 | 2475.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095.5 | 1252 | 1565 | 6260 | 5477.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 163.9479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.2849 | 0.3256 | 0.407 | 1.628 | 1.4245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10069 | 0.11507 | 0.14384 | 0.57536 | 0.50344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10069 | 0.11507 | 0.14384 | 0.57536 | 0.50344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22276 | 0.25458 | 0.31822 | 1.2729 | 1.1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 2.4234 | 2.7696 | 3.462 | 13.8478 | 12.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85646 | 0.97881 | 1.2235 | 4.8941 | 4.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85646 | 0.97881 | 1.2235 | 4.8941 | 4.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8948 | 2.1655 | 2.7068 | 10.8273 | 9.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 25.98 | 24.067 | 22.8747 | 22.4685 | 20.9373 | 19.7646 | 18.592 | 17.4193 | 16.2467 | 15.0741 | 13.9014 | 12.7288 | 11.5562 | 10.3835 | 9.2109 | 8.0382 | 6.8656 | 5.693 | 4.5203 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1403.8283 | 1604.3752 | 2005.469 | 8021.8758 | 7019.1414 | 231.3379 | 229.4249 | 228.2326 | 227.8264 | 226.2952 | 225.1225 | 223.9499 | 222.7773 | 221.6046 | 220.432 | 219.2593 | 218.0867 | 216.9141 | 215.7414 | 214.5688 | 709.5333 | 779.2374 | 919.8182 | 3044.9477 | 2689.3913 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 704.8427 | 775.7195 | 917.473 | 3043.775 | 2689.3913 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 1306.3231 | 1463.1256 | 1776.7306 | 6480.8058 | 5696.7932 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 208.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Peckforton Group BHs rehabilitation and treatment enhancement | GRD18 | GW enhancement | Y | 2025-26 | Capacity | 36 | 313480.1702 | 68390.8669 | 44856.808 | 0 | 2783.4797 | 93.4371 | 116124.5917 | 36.1259 | 37.0437 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 3525.41 | 4029.04 | 5036.3 | 20145.2 | 17627.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1611.75 | 1842 | 2302.5 | 9210 | 8058.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1611.75 | 1842 | 2302.5 | 9210 | 8058.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3416.35 | 3904.4 | 4880.5 | 19522 | 17081.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 1876.2416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.3647 | 0.4168 | 0.521 | 2.084 | 1.8235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16673 | 0.19055 | 0.23819 | 0.95276 | 0.83367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16673 | 0.19055 | 0.23819 | 0.95276 | 0.83367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35342 | 0.40391 | 0.50488 | 2.0195 | 1.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 3.7887 | 4.3299 | 5.4124 | 21.6494 | 18.9433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7321 | 1.9795 | 2.4744 | 9.8977 | 8.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7321 | 1.9795 | 2.4744 | 9.8977 | 8.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6714 | 4.1959 | 5.2449 | 20.9797 | 18.3572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 300.5516 | 278.4213 | 264.6282 | 259.9284 | 242.2147 | 228.6489 | 215.0831 | 201.5173 | 187.9515 | 174.3857 | 160.8199 | 147.2542 | 133.6884 | 120.1226 | 106.5568 | 92.991 | 79.4252 | 65.8594 | 52.2937 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 38.7279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 3529.5634 | 4033.7867 | 5042.2334 | 20168.9334 | 17647.8168 | 2184.4132 | 2162.2829 | 2148.4898 | 2143.79 | 2126.0763 | 2112.5105 | 2098.9447 | 2085.3789 | 2071.8131 | 2058.2473 | 2044.6815 | 2031.1158 | 2017.55 | 2003.9842 | 1990.4184 | 3590.5014 | 3807.4569 | 4254.9337 | 11157.0057 | 9990.8336 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 3536.2383 | 3766.7596 | 4227.8021 | 11143.4399 | 9990.8336 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 5342.9643 | 5831.5893 | 6808.8393 | 21467.5887 | 19024.4638 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 1922.5895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | New WTW on the River Weaver near Nantwich | UNK01 | SW new | N | 2030-31 | Capacity | 20 | 145433.0168 | 77855.1032 | 23611.9468 | 0 | 650.4476 | 75.0447 | 102192.5423 | 69.7689 | 70.2678 | 1 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 1252.36 | 1878.54 | 3757.08 | 4383.26 | 5635.62 | 6261.8 | 8140.34 | 12523.6 | 12523.6 | 6261.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.24 | 892.86 | 1785.72 | 2083.34 | 2678.58 | 2976.2 | 3869.06 | 5952.4 | 5952.4 | 2976.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.24 | 892.86 | 1785.72 | 2083.34 | 2678.58 | 2976.2 | 3869.06 | 5952.4 | 5952.4 | 2976.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.66 | 1847.49 | 3694.98 | 4310.81 | 5542.47 | 6158.3 | 8005.79 | 12316.6 | 12316.6 | 6158.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 340.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 845.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.14 | 0.21 | 0.42 | 0.49 | 0.63 | 0.7 | 0.91 | 1.4 | 1.4 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066541 | 0.099812 | 0.19962 | 0.23289 | 0.29944 | 0.33271 | 0.43252 | 0.66541 | 0.66541 | 0.33271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066541 | 0.099812 | 0.19962 | 0.23289 | 0.29944 | 0.33271 | 0.43252 | 0.66541 | 0.66541 | 0.33271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13769 | 0.20653 | 0.41306 | 0.4819 | 0.61959 | 0.68843 | 0.89496 | 1.3769 | 1.3769 | 0.68843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 2.7501 | 4.1251 | 8.2502 | 9.6252 | 12.3753 | 13.7503 | 17.8754 | 27.5006 | 27.5006 | 13.7503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3071 | 1.9606 | 3.9213 | 4.5748 | 5.8819 | 6.5355 | 8.4961 | 13.0709 | 13.0709 | 6.5355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3071 | 1.9606 | 3.9213 | 4.5748 | 5.8819 | 6.5355 | 8.4961 | 13.0709 | 13.0709 | 6.5355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7046 | 4.0569 | 8.1138 | 9.4661 | 12.1707 | 13.523 | 17.58 | 27.0461 | 27.0461 | 13.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5527 | 62.6042 | 58.6556 | 54.707 | 50.7584 | 46.8098 | 42.8612 | 38.9126 | 34.964 | 31.0154 | 27.0669 | 23.1183 | 19.1697 | 15.2211 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 11.2725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1255.2501 | 1882.8751 | 3765.7502 | 4393.3752 | 5648.6253 | 6276.2503 | 8159.1254 | 12552.5006 | 12552.5006 | 6276.2503 | 1255.0827 | 1251.1342 | 1247.1856 | 1243.237 | 1239.2884 | 1235.3398 | 1231.3912 | 1227.4426 | 1223.494 | 1219.5454 | 1812.2105 | 2106.5687 | 2997.5406 | 3291.8988 | 3884.5638 | 4182.8707 | 5077.7911 | 7165.9388 | 7165.9388 | 4182.8707 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1796.4161 | 2094.723 | 2989.6434 | 3287.9502 | 3884.5638 | 4182.8707 | 5077.7911 | 7165.9388 | 7165.9388 | 4182.8707 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 2434.3048 | 3051.5559 | 4903.3094 | 5520.5605 | 6755.0628 | 7372.314 | 9224.0674 | 13544.8255 | 13544.8255 | 7372.314 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 1199.8025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Support WTW L from the River Weaver | UNK03 | SW enhancement | N | 2030-31 | Capacity | 20 | 145433.0168 | 135026.1918 | 27666.1412 | 0 | 1054.2643 | 313.3046 | 164059.9018 | 111.8675 | 112.8079 | 1 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 2851.7 | 4277.55 | 8555.1 | 9980.95 | 12832.65 | 14258.5 | 18536.05 | 28517 | 28517 | 14258.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.26 | 618.39 | 1236.78 | 1442.91 | 1855.17 | 2061.3 | 2679.69 | 4122.6 | 4122.6 | 2061.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.26 | 618.39 | 1236.78 | 1442.91 | 1855.17 | 2061.3 | 2679.69 | 4122.6 | 4122.6 | 2061.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.78 | 1243.17 | 2486.34 | 2900.73 | 3729.51 | 4143.9 | 5387.07 | 8287.8 | 8287.8 | 4143.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 1140.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.3098 | 0.4647 | 0.9294 | 1.0843 | 1.3941 | 1.549 | 2.0137 | 3.098 | 3.098 | 1.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044787 | 0.06718 | 0.13436 | 0.15675 | 0.20154 | 0.22393 | 0.29111 | 0.44787 | 0.44787 | 0.22393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044787 | 0.06718 | 0.13436 | 0.15675 | 0.20154 | 0.22393 | 0.29111 | 0.44787 | 0.44787 | 0.22393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090036 | 0.13505 | 0.27011 | 0.31513 | 0.40516 | 0.45018 | 0.58523 | 0.90036 | 0.90036 | 0.45018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 14.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 16.1786 | 24.2679 | 48.5357 | 56.625 | 72.8036 | 80.8928 | 105.1607 | 161.7857 | 161.7857 | 80.8928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3389 | 3.5083 | 7.0166 | 8.1861 | 10.5249 | 11.6944 | 15.2027 | 23.3888 | 23.3888 | 11.6944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3389 | 3.5083 | 7.0166 | 8.1861 | 10.5249 | 11.6944 | 15.2027 | 23.3888 | 23.3888 | 11.6944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7019 | 7.0529 | 14.1058 | 16.4567 | 21.1587 | 23.5096 | 30.5625 | 47.0192 | 47.0192 | 23.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.005 | 37.6315 | 35.258 | 32.8844 | 30.5109 | 28.1374 | 25.7639 | 23.3904 | 21.0169 | 18.6434 | 16.2699 | 13.8964 | 11.5229 | 9.1494 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 6.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 2868.1884 | 4302.2826 | 8604.5651 | 10038.6593 | 12906.8477 | 14340.9418 | 18643.2244 | 28681.8837 | 28681.8837 | 14340.9418 | 1443.695 | 1441.3215 | 1438.948 | 1436.5744 | 1434.2009 | 1431.8274 | 1429.4539 | 1427.0804 | 1424.7069 | 1422.3334 | 1834.6036 | 2039.5519 | 2659.1439 | 2864.0922 | 3276.3624 | 3483.6842 | 4105.6497 | 5556.9026 | 5556.9026 | 3483.6842 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1825.1096 | 2032.4314 | 2654.3969 | 2861.7187 | 3276.3624 | 3483.6842 | 4105.6497 | 5556.9026 | 5556.9026 | 3483.6842 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 2244.0379 | 2660.8239 | 3911.1818 | 4327.9678 | 5161.5397 | 5578.3257 | 6828.6837 | 9746.1855 | 9746.1855 | 5578.3257 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 1410.4659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Tittesworth Reservoir capacity increase (Size A) | DAM05 | Reservoir enlargement | N | 2025-26 | Capacity | 5 | 43538.9125 | 3819.8572 | 3704.9825 | 0 | 125.1455 | 69.6865 | 7719.6718 | 17.283 | 17.7305 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 256.62 | 293.28 | 366.6 | 1466.4 | 1283.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.62 | 293.28 | 366.6 | 1466.4 | 1283.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 3.752 | 4.288 | 5.36 | 21.44 | 18.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.752 | 4.288 | 5.36 | 21.44 | 18.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 0.44372 | 0.5071 | 0.63388 | 2.5355 | 2.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44372 | 0.5071 | 0.63388 | 2.5355 | 2.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 13.1468 | 12.1788 | 11.5754 | 11.3698 | 10.595 | 10.0016 | 9.4082 | 8.8148 | 8.2214 | 7.628 | 7.0346 | 6.4412 | 5.8478 | 5.2544 | 4.661 | 4.0676 | 3.4742 | 2.8808 | 2.2874 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 1.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 260.8157 | 298.0751 | 372.5939 | 1490.3755 | 1304.0786 | 169.0268 | 168.0588 | 167.4554 | 167.2498 | 166.475 | 165.8816 | 165.2882 | 164.6948 | 164.1014 | 163.508 | 162.9146 | 162.3212 | 161.7278 | 161.1344 | 160.541 | 159.9476 | 159.3542 | 158.7608 | 158.1674 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 418.3898 | 455.6491 | 530.1679 | 1647.9496 | 1461.6526 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 157.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Tittesworth Reservoir capacity increase (Size B) | DAM06 | Reservoir enlargement | N | 2030-31 | Capacity | 14 | 101803.1118 | 13478.6364 | 8666.214 | 0 | 415.6 | 247.0957 | 22807.5462 | 21.7526 | 22.4036 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 285.82 | 428.73 | 857.46 | 1000.37 | 1286.19 | 1429.1 | 1857.83 | 2858.2 | 2858.2 | 1429.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285.82 | 428.73 | 857.46 | 1000.37 | 1286.19 | 1429.1 | 1857.83 | 2858.2 | 2858.2 | 1429.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 154.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 280.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 4.5934 | 6.8901 | 13.7802 | 16.0769 | 20.6703 | 22.967 | 29.8571 | 45.934 | 45.934 | 22.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5934 | 6.8901 | 13.7802 | 16.0769 | 20.6703 | 22.967 | 29.8571 | 45.934 | 45.934 | 22.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 4.5347 | 6.802 | 13.604 | 15.8714 | 20.4061 | 22.6734 | 29.4754 | 45.3468 | 45.3468 | 22.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5347 | 6.802 | 13.604 | 15.8714 | 20.4061 | 22.6734 | 29.4754 | 45.3468 | 45.3468 | 22.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.0036 | 26.3422 | 24.6807 | 23.0192 | 21.3578 | 19.6963 | 18.0349 | 16.3734 | 14.7119 | 13.0505 | 11.389 | 9.7276 | 8.0661 | 6.4046 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 4.7432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 294.9481 | 442.4221 | 884.8442 | 1032.3183 | 1327.2664 | 1474.7404 | 1917.1625 | 2949.4808 | 2949.4808 | 1474.7404 | 464.5336 | 462.8722 | 461.2107 | 459.5492 | 457.8878 | 456.2263 | 454.5649 | 452.9034 | 451.2419 | 449.5805 | 447.919 | 446.2576 | 444.5961 | 442.9346 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 736.2212 | 883.6953 | 1326.1174 | 1473.5914 | 1768.5395 | 1916.0136 | 2358.4357 | 3390.754 | 3390.754 | 1916.0136 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 441.2732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | New WTW on the River Trent near Stafford, Staffordshire | WTW29 | SW new | N | 2030-31 | Capacity | 22.5 | 163612.1439 | 112126.8416 | 48192.1189 | 0 | 2008.4759 | 133.2607 | 162460.6971 | 97.9872 | 99.2962 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 2278.6 | 3417.9 | 6835.8 | 7975.1 | 10253.7 | 11393 | 14810.9 | 22786 | 22786 | 11393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430.4 | 645.6 | 1291.2 | 1506.4 | 1936.8 | 2152 | 2797.6 | 4304 | 4304 | 2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430.4 | 645.6 | 1291.2 | 1506.4 | 1936.8 | 2152 | 2797.6 | 4304 | 4304 | 2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827.4 | 1241.1 | 2482.2 | 2895.9 | 3723.3 | 4137 | 5378.1 | 8274 | 8274 | 4137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.4166 | 0.6249 | 1.2498 | 1.4581 | 1.8747 | 2.083 | 2.7079 | 4.166 | 4.166 | 2.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078691 | 0.11804 | 0.23607 | 0.27542 | 0.35411 | 0.39345 | 0.51149 | 0.78691 | 0.78691 | 0.39345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078691 | 0.11804 | 0.23607 | 0.27542 | 0.35411 | 0.39345 | 0.51149 | 0.78691 | 0.78691 | 0.39345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15127 | 0.22691 | 0.45382 | 0.52946 | 0.68074 | 0.75637 | 0.98329 | 1.5127 | 1.5127 | 0.75637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 12.9994 | 19.4991 | 38.9982 | 45.498 | 58.4974 | 64.9971 | 84.4962 | 129.9942 | 129.9942 | 64.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4554 | 3.6831 | 7.3663 | 8.594 | 11.0494 | 12.2772 | 15.9603 | 24.5543 | 24.5543 | 12.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4554 | 3.6831 | 7.3663 | 8.594 | 11.0494 | 12.2772 | 15.9603 | 24.5543 | 24.5543 | 12.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7203 | 7.0805 | 14.161 | 16.5211 | 21.2414 | 23.6016 | 30.6821 | 47.2032 | 47.2032 | 23.6016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.9889 | 178.7168 | 167.4447 | 156.1727 | 144.9006 | 133.6285 | 122.3564 | 111.0843 | 99.8122 | 88.5402 | 77.2681 | 65.996 | 54.7239 | 43.4518 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 32.1798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 2292.016 | 3438.024 | 6876.048 | 8022.0561 | 10314.0721 | 11460.0801 | 14898.1041 | 22920.1602 | 22920.1602 | 11460.0801 | 2614.6489 | 2603.3768 | 2592.1047 | 2580.8327 | 2569.5606 | 2558.2885 | 2547.0164 | 2535.7443 | 2524.4722 | 2513.2002 | 2934.8622 | 3140.0572 | 3778.1863 | 3983.3813 | 4405.0433 | 4621.5104 | 5270.9116 | 6786.181 | 6786.181 | 4621.5104 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2889.7739 | 3106.2409 | 3755.6421 | 3972.1092 | 4405.0433 | 4621.5104 | 5270.9116 | 6786.181 | 6786.181 | 4621.5104 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 3289.1113 | 3705.2471 | 4953.6545 | 5369.7903 | 6202.0619 | 6618.1977 | 7866.6051 | 10779.5557 | 10779.5557 | 6618.1977 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 2456.8398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | New WTW on the River Trent near Little Haywood supported by raw water augmentation of the River Trent | WTW01 | Effluent reuse | N | 2030-31 | Capacity | 13 | 94531.4609 | 117221.4487 | 29263.9121 | 0 | 920.902 | 127.0853 | 147533.3481 | 154.9594 | 156.068 | 1 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 2126.9 | 3190.35 | 6380.7 | 7444.15 | 9571.05 | 10634.5 | 13824.85 | 21269 | 21269 | 10634.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.86 | 893.79 | 1787.58 | 2085.51 | 2681.37 | 2979.3 | 3873.09 | 5958.6 | 5958.6 | 2979.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.86 | 893.79 | 1787.58 | 2085.51 | 2681.37 | 2979.3 | 3873.09 | 5958.6 | 5958.6 | 2979.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1801.06 | 2701.59 | 5403.18 | 6303.71 | 8104.77 | 9005.3 | 11706.89 | 18010.6 | 18010.6 | 9005.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 211.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 1257.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.5744 | 0.8616 | 1.7232 | 2.0104 | 2.5848 | 2.872 | 3.7336 | 5.744 | 5.744 | 2.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16092 | 0.24138 | 0.48276 | 0.56322 | 0.72414 | 0.8046 | 1.046 | 1.6092 | 1.6092 | 0.8046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16092 | 0.24138 | 0.48276 | 0.56322 | 0.72414 | 0.8046 | 1.046 | 1.6092 | 1.6092 | 0.8046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4864 | 0.7296 | 1.4592 | 1.7024 | 2.1888 | 2.432 | 3.1616 | 4.864 | 4.864 | 2.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 6.5436 | 9.8154 | 19.6308 | 22.9026 | 29.4462 | 32.718 | 42.5333 | 65.4359 | 65.4359 | 32.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8332 | 2.7498 | 5.4996 | 6.4163 | 8.2495 | 9.1661 | 11.9159 | 18.3321 | 18.3321 | 9.1661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8332 | 2.7498 | 5.4996 | 6.4163 | 8.2495 | 9.1661 | 11.9159 | 18.3321 | 18.3321 | 9.1661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5411 | 8.3117 | 16.6234 | 19.3939 | 24.935 | 27.7056 | 36.0173 | 55.4112 | 55.4112 | 27.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7643 | 73.1505 | 68.5368 | 63.923 | 59.3092 | 54.6955 | 50.0817 | 45.4679 | 40.8541 | 36.2404 | 31.6266 | 27.0128 | 22.399 | 17.7853 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 13.1715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 2134.018 | 3201.027 | 6402.054 | 7469.063 | 9603.081 | 10670.09 | 13871.1169 | 21340.1799 | 21340.1799 | 10670.09 | 1551.4543 | 1546.8405 | 1542.2268 | 1537.613 | 1532.9992 | 1528.3855 | 1523.7717 | 1519.1579 | 1514.5441 | 1509.9304 | 2103.1707 | 2397.484 | 3289.6514 | 3583.9647 | 4177.2051 | 4476.1322 | 5372.9134 | 7465.4028 | 7465.4028 | 4476.1322 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 2084.7156 | 2383.6427 | 3280.4239 | 3579.351 | 4177.2051 | 4476.1322 | 5372.9134 | 7465.4028 | 7465.4028 | 4476.1322 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 3293.949 | 4197.4928 | 6908.124 | 7811.6678 | 9618.7553 | 10522.2991 | 13232.9304 | 19557.7367 | 19557.7367 | 10522.2991 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 1486.8615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.2a | Options to increase raw imports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Raw water import from CRT to Milford WTW | RAW01 | SW new | N | 2030-31 | Capacity | 15 | 109074.7626 | 88400.6129 | 58693.1796 | 0 | 907.3724 | 221.8218 | 148222.9867 | 134.8559 | 135.8912 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 1636.18 | 2454.27 | 4908.54 | 5726.63 | 7362.81 | 8180.9 | 10635.17 | 16361.8 | 16361.8 | 8180.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435.84 | 653.76 | 1307.52 | 1525.44 | 1961.28 | 2179.2 | 2832.96 | 4358.4 | 4358.4 | 2179.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435.84 | 653.76 | 1307.52 | 1525.44 | 1961.28 | 2179.2 | 2832.96 | 4358.4 | 4358.4 | 2179.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.02 | 1822.53 | 3645.06 | 4252.57 | 5467.59 | 6075.1 | 7897.63 | 12150.2 | 12150.2 | 6075.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 177.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 2768.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 1.9264 | 2.8896 | 5.7792 | 6.7424 | 8.6688 | 9.632 | 12.5216 | 19.264 | 19.264 | 9.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51315 | 0.76972 | 1.5394 | 1.796 | 2.3092 | 2.5657 | 3.3355 | 5.1315 | 5.1315 | 2.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51315 | 0.76972 | 1.5394 | 1.796 | 2.3092 | 2.5657 | 3.3355 | 5.1315 | 5.1315 | 2.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4305 | 2.1458 | 4.2916 | 5.0069 | 6.4374 | 7.1527 | 9.2985 | 14.3054 | 14.3054 | 7.1527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 5.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 7.431 | 11.1465 | 22.2931 | 26.0086 | 33.4396 | 37.1551 | 48.3017 | 74.3102 | 74.3102 | 37.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9795 | 2.9692 | 5.9384 | 6.9281 | 8.9075 | 9.8973 | 12.8664 | 19.7945 | 19.7945 | 9.8973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9795 | 2.9692 | 5.9384 | 6.9281 | 8.9075 | 9.8973 | 12.8664 | 19.7945 | 19.7945 | 9.8973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5182 | 8.2774 | 16.5547 | 19.3139 | 24.8321 | 27.5912 | 35.8686 | 55.1825 | 55.1825 | 27.5912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2169 | 66.0509 | 61.8849 | 57.719 | 53.553 | 49.387 | 45.221 | 41.055 | 36.889 | 32.7231 | 28.5571 | 24.3911 | 20.2251 | 16.0591 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 11.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1645.5374 | 2468.3061 | 4936.6123 | 5759.381 | 7404.9184 | 8227.6871 | 10695.9933 | 16455.3742 | 16455.3742 | 8227.6871 | 3022.2269 | 3018.0609 | 3013.8949 | 3009.729 | 3005.563 | 3001.397 | 2997.231 | 2993.065 | 2988.899 | 2984.7331 | 3418.8997 | 3633.9 | 4287.2329 | 4502.2332 | 4936.3998 | 5155.5661 | 5813.065 | 7347.2291 | 7347.2291 | 5155.5661 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 3402.2357 | 3621.402 | 4278.9009 | 4498.0672 | 4936.3998 | 5155.5661 | 5813.065 | 7347.2291 | 7347.2291 | 5155.5661 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 4185.8719 | 4796.8563 | 6629.8095 | 7240.7939 | 8462.7626 | 9073.747 | 10906.7002 | 15183.5909 | 15183.5909 | 9073.747 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 2963.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Carsington reservoir to Tittesworth transfer solution | RAW17 | Bulk supply | N | 2025-26 | Capacity | 10 | 87077.825 | 168298.9601 | 16964.6689 | 0 | 999.45 | 119.8712 | 186382.9502 | 212.7564 | 214.0418 | 1 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 11924.5 | 13628 | 17035 | 68140 | 59622.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.8 | 1147.2 | 1434 | 5736 | 5019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.8 | 1147.2 | 1434 | 5736 | 5019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1986.32 | 2270.08 | 2837.6 | 11350.4 | 9931.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 593.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 1.2586 | 1.4384 | 1.798 | 7.192 | 6.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10595 | 0.12108 | 0.15135 | 0.60542 | 0.52974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10595 | 0.12108 | 0.15135 | 0.60542 | 0.52974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20965 | 0.2396 | 0.2995 | 1.198 | 1.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 50.7202 | 57.9659 | 72.4574 | 289.8294 | 253.6008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2696 | 4.8795 | 6.0994 | 24.3977 | 21.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2696 | 4.8795 | 6.0994 | 24.3977 | 21.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4487 | 9.6557 | 12.0696 | 48.2783 | 42.2435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 31.4528 | 29.1369 | 27.6934 | 27.2016 | 25.3478 | 23.9282 | 22.5085 | 21.0888 | 19.6692 | 18.2495 | 16.8299 | 15.4102 | 13.9905 | 12.5709 | 11.1512 | 9.7315 | 8.3119 | 6.8922 | 5.4725 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 4.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 11976.4788 | 13687.4043 | 17109.2554 | 68437.0214 | 59882.3938 | 746.8328 | 744.5169 | 743.0734 | 742.5816 | 740.7278 | 739.3082 | 737.8885 | 736.4688 | 735.0492 | 733.6295 | 732.2099 | 730.7902 | 729.3705 | 727.9509 | 726.5312 | 1733.2871 | 1875.8925 | 2162.523 | 6481.8557 | 5760.3106 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 1727.6084 | 1871.6335 | 2159.6837 | 6480.436 | 5760.3106 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 2714.4112 | 2999.4081 | 3569.4019 | 12119.3091 | 10694.3246 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 719.4329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | New WTW on River Dove near Uttoxeter supported by Carsington reservoir and deploying to Stoke (Size A) | GRD20 | SW new | N | 2035-36 | Capacity | 18 | 109124.3973 | 84071.9659 | 21783.3557 | 0 | 977.5128 | 116.4878 | 106949.3223 | 97.0043 | 98.0068 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 850.91 | 1701.82 | 1701.82 | 2552.73 | 2552.73 | 4254.55 | 5105.46 | 8509.1 | 8509.1 | 8509.1 | 8509.1 | 8509.1 | 8509.1 | 8509.1 | 6807.28 | 0 | 0 | 0 | 0 | 0 | 247.6 | 495.2 | 495.2 | 742.8 | 742.8 | 1238 | 1485.6 | 2476 | 2476 | 2476 | 2476 | 2476 | 2476 | 2476 | 1980.8 | 0 | 0 | 0 | 0 | 0 | 247.6 | 495.2 | 495.2 | 742.8 | 742.8 | 1238 | 1485.6 | 2476 | 2476 | 2476 | 2476 | 2476 | 2476 | 2476 | 1980.8 | 0 | 0 | 0 | 0 | 0 | 603.91 | 1207.82 | 1207.82 | 1811.73 | 1811.73 | 3019.55 | 3623.46 | 6039.1 | 6039.1 | 6039.1 | 6039.1 | 6039.1 | 6039.1 | 6039.1 | 4831.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.0947 | 0.1894 | 0.1894 | 0.2841 | 0.2841 | 0.4735 | 0.5682 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.7576 | 0 | 0 | 0 | 0 | 0 | 0.027556 | 0.055112 | 0.055112 | 0.082668 | 0.082668 | 0.13778 | 0.16534 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.22045 | 0 | 0 | 0 | 0 | 0 | 0.027556 | 0.055112 | 0.055112 | 0.082668 | 0.082668 | 0.13778 | 0.16534 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.27556 | 0.22045 | 0 | 0 | 0 | 0 | 0 | 0.067211 | 0.13442 | 0.13442 | 0.20163 | 0.20163 | 0.33605 | 0.40326 | 0.67211 | 0.67211 | 0.67211 | 0.67211 | 0.67211 | 0.67211 | 0.67211 | 0.53769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 5.4124 | 10.8247 | 10.8247 | 16.2371 | 16.2371 | 27.0618 | 32.4742 | 54.1236 | 54.1236 | 54.1236 | 54.1236 | 54.1236 | 54.1236 | 54.1236 | 43.2989 | 0 | 0 | 0 | 0 | 0 | 1.5749 | 3.1498 | 3.1498 | 4.7247 | 4.7247 | 7.8745 | 9.4494 | 15.749 | 15.749 | 15.749 | 15.749 | 15.749 | 15.749 | 15.749 | 12.5992 | 0 | 0 | 0 | 0 | 0 | 1.5749 | 3.1498 | 3.1498 | 4.7247 | 4.7247 | 7.8745 | 9.4494 | 15.749 | 15.749 | 15.749 | 15.749 | 15.749 | 15.749 | 15.749 | 12.5992 | 0 | 0 | 0 | 0 | 0 | 3.8413 | 7.6825 | 7.6825 | 11.5238 | 11.5238 | 19.2064 | 23.0476 | 38.4127 | 38.4127 | 38.4127 | 38.4127 | 38.4127 | 38.4127 | 38.4127 | 30.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9077 | 66.7577 | 60.6076 | 54.4576 | 48.3075 | 42.1575 | 36.0074 | 29.8574 | 23.7073 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 17.5573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 856.4171 | 1712.8341 | 1712.8341 | 2569.2512 | 2569.2512 | 4282.0853 | 5138.5024 | 8564.1706 | 8564.1706 | 8564.1706 | 8564.1706 | 8564.1706 | 8564.1706 | 8564.1706 | 6851.3365 | 1390.8577 | 1384.7077 | 1378.5576 | 1372.4076 | 1366.2575 | 1609.3099 | 1852.3623 | 1846.2123 | 2089.2647 | 2083.1146 | 2581.5196 | 2830.722 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3329.1269 | 1335.5073 | 1335.5073 | 1335.5073 | 1335.5073 | 1335.5073 | 1584.7097 | 1833.9122 | 1833.9122 | 2083.1146 | 2083.1146 | 2581.5196 | 2830.722 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3827.5319 | 3329.1269 | 1335.5073 | 1335.5073 | 1335.5073 | 1335.5073 | 1335.5073 | 1943.3258 | 2551.1442 | 2551.1442 | 3158.9627 | 3158.9627 | 4374.5997 | 4982.4182 | 7413.6921 | 7413.6921 | 7413.6921 | 7413.6921 | 7413.6921 | 7413.6921 | 7413.6921 | 6198.0551 | 1335.5073 | 1335.5073 | 1335.5073 | 1335.5073 | 1335.5073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | New WTW on River Dove near Uttoxeter supported by Carsington reservoir and deploying to Stoke (Size B) | GRD21 | SW new | N | 2035-36 | Capacity | 27 | 163686.5959 | 133791.6555 | 32650.9498 | 0 | 1168.1379 | 189.9794 | 167800.7226 | 101.6837 | 102.5134 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 1438.97 | 2877.94 | 2877.94 | 4316.91 | 4316.91 | 7194.85 | 8633.82 | 14389.7 | 14389.7 | 14389.7 | 14389.7 | 14389.7 | 14389.7 | 14389.7 | 11511.76 | 0 | 0 | 0 | 0 | 0 | 328.33 | 656.66 | 656.66 | 984.99 | 984.99 | 1641.65 | 1969.98 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 2626.64 | 0 | 0 | 0 | 0 | 0 | 328.33 | 656.66 | 656.66 | 984.99 | 984.99 | 1641.65 | 1969.98 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 3283.3 | 2626.64 | 0 | 0 | 0 | 0 | 0 | 744.04 | 1488.08 | 1488.08 | 2232.12 | 2232.12 | 3720.2 | 4464.24 | 7440.4 | 7440.4 | 7440.4 | 7440.4 | 7440.4 | 7440.4 | 7440.4 | 5952.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 428.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 1537.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.1497 | 0.2994 | 0.2994 | 0.4491 | 0.4491 | 0.7485 | 0.8982 | 1.497 | 1.497 | 1.497 | 1.497 | 1.497 | 1.497 | 1.497 | 1.1976 | 0 | 0 | 0 | 0 | 0 | 0.034157 | 0.068314 | 0.068314 | 0.10247 | 0.10247 | 0.17079 | 0.20494 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.27326 | 0 | 0 | 0 | 0 | 0 | 0.034157 | 0.068314 | 0.068314 | 0.10247 | 0.10247 | 0.17079 | 0.20494 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.34157 | 0.27326 | 0 | 0 | 0 | 0 | 0 | 0.077405 | 0.15481 | 0.15481 | 0.23221 | 0.23221 | 0.38702 | 0.46443 | 0.77405 | 0.77405 | 0.77405 | 0.77405 | 0.77405 | 0.77405 | 0.77405 | 0.61924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 5.4221 | 10.8442 | 10.8442 | 16.2663 | 16.2663 | 27.1106 | 32.5327 | 54.2211 | 54.2211 | 54.2211 | 54.2211 | 54.2211 | 54.2211 | 54.2211 | 43.3769 | 0 | 0 | 0 | 0 | 0 | 1.2372 | 2.4743 | 2.4743 | 3.7115 | 3.7115 | 6.1858 | 7.423 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 9.8973 | 0 | 0 | 0 | 0 | 0 | 1.2372 | 2.4743 | 2.4743 | 3.7115 | 3.7115 | 6.1858 | 7.423 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 12.3716 | 9.8973 | 0 | 0 | 0 | 0 | 0 | 2.8036 | 5.6072 | 5.6072 | 8.4107 | 8.4107 | 14.0179 | 16.8215 | 28.0358 | 28.0358 | 28.0358 | 28.0358 | 28.0358 | 28.0358 | 28.0358 | 22.4286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3395 | 100.1163 | 90.8931 | 81.6699 | 72.4467 | 63.2235 | 54.0003 | 44.777 | 35.5538 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 26.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1444.5418 | 2889.0836 | 2889.0836 | 4333.6254 | 4333.6254 | 7222.7091 | 8667.2509 | 14445.4181 | 14445.4181 | 14445.4181 | 14445.4181 | 14445.4181 | 14445.4181 | 14445.4181 | 11556.3345 | 2085.7395 | 2076.5163 | 2067.2931 | 2058.0699 | 2048.8467 | 2369.2248 | 2689.6029 | 2680.3797 | 3000.7578 | 2991.5346 | 3650.7372 | 3980.3385 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 4639.5412 | 2002.7306 | 2002.7306 | 2002.7306 | 2002.7306 | 2002.7306 | 2332.3319 | 2661.9333 | 2661.9333 | 2991.5346 | 2991.5346 | 3650.7372 | 3980.3385 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 5298.7438 | 4639.5412 | 2002.7306 | 2002.7306 | 2002.7306 | 2002.7306 | 2002.7306 | 2749.6516 | 3496.5726 | 3496.5726 | 4243.4936 | 4243.4936 | 5737.3355 | 6484.2565 | 9471.9405 | 9471.9405 | 9471.9405 | 9471.9405 | 9471.9405 | 9471.9405 | 9471.9405 | 7978.0985 | 2002.7306 | 2002.7306 | 2002.7306 | 2002.7306 | 2002.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.3a | Options to increase potable imports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Potable water import to Peckforton and North Staffs WRZ | GRD13 | Bulk supply | N | 2025-26 | Capacity | 5 | 43538.9125 | 11254.4865 | 25278.8119 | 0 | 687.1414 | 64.6467 | 37285.0865 | 83.9095 | 85.6362 | 1 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 540.54 | 617.76 | 772.2 | 3088.8 | 2702.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.87 | 371.28 | 464.1 | 1856.4 | 1624.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.87 | 371.28 | 464.1 | 1856.4 | 1624.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518.91 | 593.04 | 741.3 | 2965.2 | 2594.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 1056.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.4466 | 0.5104 | 0.638 | 2.552 | 2.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26841 | 0.30676 | 0.38344 | 1.5338 | 1.3421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26841 | 0.30676 | 0.38344 | 1.5338 | 1.3421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42873 | 0.48998 | 0.61247 | 2.4499 | 2.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 12.0486 | 13.7698 | 17.2123 | 68.8491 | 60.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2413 | 8.2758 | 10.3448 | 41.379 | 36.2066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2413 | 8.2758 | 10.3448 | 41.379 | 36.2066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5665 | 13.2188 | 16.5235 | 66.0941 | 57.8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 48.3858 | 44.823 | 42.6025 | 41.8459 | 38.9941 | 36.8102 | 34.6262 | 32.4423 | 30.2583 | 28.0743 | 25.8904 | 23.7064 | 21.5225 | 19.3385 | 17.1546 | 14.9706 | 12.7867 | 10.6027 | 8.4188 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 6.2348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 553.0352 | 632.0402 | 790.0503 | 3160.2011 | 2765.176 | 1110.3058 | 1106.743 | 1104.5225 | 1103.7659 | 1100.9141 | 1098.7302 | 1096.5462 | 1094.3623 | 1092.1783 | 1089.9943 | 1087.8104 | 1085.6264 | 1083.4425 | 1081.2585 | 1079.0746 | 1409.2704 | 1454.5692 | 1547.3509 | 2969.6515 | 2730.0535 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1400.5345 | 1448.0174 | 1542.983 | 2967.4676 | 2730.0535 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1599.06 | 1674.9036 | 1826.5908 | 4101.8988 | 3722.6808 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 1068.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Site U to North Staffs WRZ transfer solution | GRD11 | Bulk supply | N | 2025-26 | Capacity | 15 | 130616.7376 | 153219.389 | 7233.4237 | 0 | 990.4287 | 136.2313 | 161579.4728 | 122.8425 | 123.705 | 1 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 11444.79 | 13079.76 | 16349.7 | 65398.8 | 57223.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.63 | 400.72 | 500.9 | 2003.6 | 1753.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.63 | 400.72 | 500.9 | 2003.6 | 1753.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 781.48 | 893.12 | 1116.4 | 4465.6 | 3907.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 293.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 3.9032 | 4.4608 | 5.576 | 22.304 | 19.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11958 | 0.13666 | 0.17083 | 0.68332 | 0.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11958 | 0.13666 | 0.17083 | 0.68332 | 0.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26652 | 0.3046 | 0.38074 | 1.523 | 1.3326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 30.9919 | 35.4193 | 44.2741 | 177.0963 | 154.9593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94949 | 1.0851 | 1.3564 | 5.4256 | 4.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94949 | 1.0851 | 1.3564 | 5.4256 | 4.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1162 | 2.4185 | 3.0231 | 12.0926 | 10.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 63.8282 | 59.1283 | 56.1991 | 55.201 | 51.4391 | 48.5582 | 45.6772 | 42.7962 | 39.9153 | 37.0343 | 34.1533 | 31.2724 | 28.3914 | 25.5104 | 22.6295 | 19.7485 | 16.8675 | 13.9866 | 11.1056 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 8.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 11479.6851 | 13119.6401 | 16399.5501 | 65598.2003 | 57398.4253 | 370.5482 | 365.8483 | 362.9191 | 361.921 | 358.1591 | 355.2782 | 352.3972 | 349.5162 | 346.6353 | 343.7543 | 340.8733 | 337.9924 | 335.1114 | 332.2304 | 329.3495 | 678.1676 | 725.5293 | 823.1338 | 2327.5346 | 2073.44 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 666.6437 | 716.8864 | 817.3719 | 2324.6536 | 2073.44 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 1098.8074 | 1210.7878 | 1434.7485 | 4794.1602 | 4234.2583 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 314.9446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.4a | Options to reduce raw water losses and operational use | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.5a | Options to reduce raw water exports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.6a | Options to reduce potable water exports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.7a | Other options to increase Deployable Output | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Improve Site L outputs during low raw water periods | UNK07 | SW enhancement | Y | 2025-26 | Capacity | 7 | 60954.4775 | 15950.705 | 11372.6025 | 0 | 284.2595 | 22.6348 | 27630.2019 | 44.8258 | 45.3292 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 713.2259 | 815.1154 | 1018.8942 | 4075.5768 | 3566.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537.1484 | 613.8838 | 767.3548 | 3069.4192 | 2685.7418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537.1484 | 613.8838 | 767.3548 | 3069.4192 | 2685.7418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 692.5885 | 791.5298 | 989.4122 | 3957.6488 | 3462.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| **STW | [17 empty] | Fixed opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 399.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0.1267 | 0.1448 | 0.181 | 0.724 | 0.6335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095421 | 0.10905 | 0.13632 | 0.54526 | 0.4771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095421 | 0.10905 | 0.13632 | 0.54526 | 0.4771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12303 | 0.14061 | 0.17576 | 0.70305 | 0.61517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 5.2905 | 6.0462 | 7.5578 | 30.2312 | 26.4523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9844 | 4.5536 | 5.692 | 22.7679 | 19.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9844 | 4.5536 | 5.692 | 22.7679 | 19.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1374 | 5.8713 | 7.3391 | 29.3565 | 25.6869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 18.4039 | 17.0488 | 16.2042 | 15.9164 | 14.8318 | 14.0011 | 13.1704 | 12.3397 | 11.509 | 10.6783 | 9.8476 | 9.0169 | 8.1863 | 7.3556 | 6.5249 | 5.6942 | 4.8635 | 4.0328 | 3.2021 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 718.6431 | 821.3064 | 1026.633 | 4106.532 | 3593.2155 | 495.9339 | 494.5788 | 493.7342 | 493.4464 | 492.3618 | 491.5311 | 490.7004 | 489.8697 | 489.039 | 488.2083 | 487.3776 | 486.5469 | 485.7163 | 484.8856 | 484.0549 | 1024.4524 | 1100.94 | 1254.7459 | 3573.4645 | 3186.0423 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 1021.1296 | 1098.4479 | 1253.0845 | 3572.6338 | 3186.0423 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 1177.7504 | 1277.4431 | 1476.8285 | 4467.6098 | 3969.1462 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 479.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59a | DISTRIBUTION SIDE | bar: 1 Year 1 to 80 Year 80
59.1a | Options to reduce Distribution Losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Active Leakage Control - Supply demand balance scenario | ALC1 | Active leakage management | N | 2020/21 | Capacity | 7.5432 | 46967.4347 | 44212.4587 | 2777.8177 | -10279.0629 | 12.8324 | 8551.8495 | 45275.8954 | 78.1631 | 96.3985 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0.013899 | 0.055684 | 0.12547 | 0.22337 | 0.34948 | 0.50105 | 0.67498 | 0.8714 | 1.0904 | 1.3322 | 1.5991 | 1.8937 | 2.2161 | 2.5666 | 2.9452 | 3.351 | 3.7828 | 4.2407 | 4.7247 | 5.2351 | 5.7718 | 6.3353 | 6.9257 | 7.5432 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 8.1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed capex | Input | £000s | 33.984 | 34.1722 | 34.399 | 34.6436 | 34.9065 | 35.1721 | 35.4332 | 35.7065 | 35.9982 | 36.3096 | 36.6549 | 37.0431 | 37.464 | 37.9165 | 38.404 | 38.9236 | 39.4752 | 40.0711 | 40.72 | 41.4303 | 42.2115 | 43.0809 | 44.0552 | 45.1583 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 46.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 725.5265 | 733.8848 | 746.0051 | 761.4825 | 780.3894 | 802.1601 | 826.3748 | 853.4799 | 883.7063 | 917.1969 | 954.6403 | 996.6862 | 1043.3348 | 1094.8132 | 1151.4905 | 1213.5237 | 1281.1371 | 1355.058 | 1436.045 | 1524.9738 | 1622.8999 | 1731.3701 | 1852.1837 | 1987.7956 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 2141.6741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Fixed opex | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Variable opex | Input | £000s | 80.4535 | 80.8989 | 81.436 | 82.0149 | 82.6373 | 83.2662 | 83.8842 | 84.5313 | 85.2219 | 85.9589 | 86.7764 | 87.6954 | 88.692 | 89.7633 | 90.9172 | 92.1473 | 93.4533 | 94.8639 | 96.4002 | 98.0816 | 99.9311 | 101.9895 | 104.2958 | 106.9073 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 109.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 0 | 1.1103 | 4.4482 | 10.0228 | 17.843 | 27.9173 | 40.0249 | 53.919 | 69.6096 | 87.107 | 106.4216 | 127.7388 | 151.2705 | 177.0281 | 205.0233 | 235.2676 | 267.6857 | 302.1776 | 338.7528 | 377.4206 | 418.1902 | 461.0598 | 506.0752 | 553.2425 | 602.5677 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 654.0571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Variable env & social | Input | £000s | 0.68498 | 2.7473 | 6.2016 | 11.069 | 17.3768 | 25.0147 | 33.8576 | 43.9468 | 55.33 | 68.0623 | 82.3256 | 98.3378 | 116.201 | 136.0349 | 157.981 | 182.1415 | 208.6235 | 237.6493 | 269.4892 | 304.4745 | 343.0082 | 385.6496 | 433.0846 | 486.2331 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 546.3787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Variable carbon costs | Input | £000s | 0.72046 | 0.69995 | 0.68077 | 0.66243 | 0.64488 | 0.62782 | 0.61109 | 0.59498 | 0.57955 | 0.5648 | 0.55089 | 0.5379 | 0.52561 | 0.51397 | 0.50298 | 0.49254 | 0.48263 | 0.47335 | 0.46475 | 0.45686 | 0.44974 | 0.44348 | 0.43817 | 0.43396 | 0.43105 | 0.41647 | 0.40239 | 0.38878 | 0.37564 | 0.36293 | 0.40549 | 0.39368 | 0.38221 | 0.37108 | 0.36027 | 0.34978 | 0.33959 | 0.3297 | 0.3201 | 0.31077 | 0.30172 | 0.29293 | 0.2844 | 0.27612 | 0.26808 | 0.26027 | 0.25269 | 0.24533 | 0.23818 | 0.23125 | 0.22451 | 0.21797 | 0.21162 | 0.20546 | 0.19947 | 0.19366 | 0.18802 | 0.18255 | 0.17723 | 0.17207 | 0.16706 | 0.16219 | 0.15747 | 0.15288 | 0.14843 | 0.1441 | 0.13991 | 0.13583 | 0.13188 | 0.12804 | 0.12431 | 0.12069 | 0.11717 | 0.11376 | 0.11044 | 0.15446 | 0.15069 | 0.14701 | 0.14343 | 0.13993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 841.3695 | 853.5133 | 873.1707 | 899.8952 | 933.7979 | 974.1582 | 1020.1858 | 1072.1784 | 1130.4455 | 1195.1995 | 1267.3697 | 1348.0393 | 1437.4879 | 1536.07 | 1644.3191 | 1762.4963 | 1890.8574 | 2030.2932 | 2181.872 | 2346.8376 | 2526.6906 | 2723.5934 | 2940.1326 | 3179.7708 | 3447.3862 | 3498.8609 | 3498.8469 | 3498.8333 | 3498.8201 | 3498.8074 | 3498.85 | 3498.8382 | 3498.8267 | 3498.8156 | 3498.8047 | 3498.7943 | 3498.7841 | 3498.7742 | 3498.7646 | 3498.7552 | 3498.7462 | 3498.7374 | 3498.7289 | 3498.7206 | 3498.7125 | 3498.7047 | 3498.6972 | 3498.6898 | 3498.6827 | 3498.6757 | 3498.669 | 3498.6624 | 3498.6561 | 3498.6499 | 3498.6439 | 3498.6381 | 3498.6325 | 3498.627 | 3498.6217 | 3498.6165 | 3498.6115 | 3498.6067 | 3498.6019 | 3498.5974 | 3498.5929 | 3498.5886 | 3498.5844 | 3498.5803 | 3498.5763 | 3498.5725 | 3498.5688 | 3498.5652 | 3498.5616 | 3498.5582 | 3498.5549 | 3498.5989 | 3498.5952 | 3498.5915 | 3498.5879 | 3498.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Active Leakage Control - National Infrustructure commision scenario | ALC2 | Active leakage management | Y | 2020/21 | Capacity | 18.6466 | 118773.9544 | 160171.33 | 4349.0956 | -25994.2864 | 18.221 | 56507.0376 | 195051.3979 | 116.6301 | 164.2207 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0.013899 | 0.055684 | 0.12547 | 0.22337 | 0.34948 | 1.3833 | 2.4396 | 3.5183 | 4.6196 | 5.7437 | 6.7605 | 7.8051 | 8.8775 | 9.9779 | 11.1065 | 11.9373 | 12.794 | 13.6769 | 14.5859 | 15.5212 | 16.4404 | 17.3864 | 18.3593 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466 | 18.6466
[19 empty] | Fixed capex | Input | £000s | 33.984 | 34.1722 | 34.399 | 34.6436 | 34.9065 | 40.2876 | 41.2444 | 42.3122 | 43.5262 | 44.9297 | 45.6768 | 47.4603 | 49.6778 | 52.6038 | 57.0144 | 63.345 | 65.0741 | 67.0611 | 69.3975 | 72.2279 | 75.2762 | 79.9148 | 87.6644 | 86.5228 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242 | 83.8242
[19 empty] | Variable capex | Input | £000s | 725.5265 | 733.8848 | 746.0051 | 761.4825 | 780.3894 | 1007.6736 | 1150.4063 | 1307.0375 | 1480.7761 | 1676.0152 | 1857.3993 | 2086.0754 | 2359.3794 | 2702.8579 | 3184.9428 | 3838.0039 | 4187.459 | 4591.7909 | 5068.413 | 5645.2296 | 6328.8138 | 7255.4493 | 8754.3231 | 9594.2185 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202 | 9536.7202
[19 empty] | Financing costs | Input | £000s
[19 empty] | Fixed opex | Input | £000s
[19 empty] | Variable opex | Input | £000s | 80.4535 | 80.8989 | 81.436 | 82.0149 | 82.6373 | 95.3766 | 97.6417 | 100.1696 | 103.0435 | 106.3662 | 108.1349 | 112.3572 | 117.6069 | 124.5337 | 134.9754 | 149.9623 | 154.0559 | 158.7598 | 164.2911 | 170.9917 | 178.2081 | 189.1895 | 207.536 | 204.8333 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446 | 198.4446
[19 empty] | Opex savings | Input | £000s | 0 | 1.1103 | 4.4482 | 10.0228 | 17.843 | 27.9173 | 110.5049 | 194.879 | 281.0496 | 369.027 | 458.8215 | 540.0468 | 623.4864 | 709.152 | 797.0552 | 887.2075 | 953.5734 | 1022.0132 | 1092.5363 | 1165.1519 | 1239.8694 | 1313.2921 | 1388.8606 | 1466.5809 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278 | 1489.5278
[19 empty] | Fixed env & social | Input | £000s
[19 empty] | Variable env & social | Input | £000s | 0.68498 | 2.7473 | 6.2016 | 11.069 | 17.3768 | 70.7732 | 128.7756 | 192.2456 | 262.35 | 340.7323 | 419.1767 | 509.5728 | 616.7423 | 750.0244 | 934.0208 | 1179.6802 | 1327.8846 | 1499.5007 | 1701.8583 | 1946.7273 | 2240.0121 | 2632.4591 | 3264.7696 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808 | 3674.4808
[19 empty] | Fixed carbon costs | Input | £000s
[19 empty] | Variable carbon costs | Input | £000s | 0.72046 | 0.69995 | 0.68077 | 0.66243 | 0.64488 | 0.71913 | 0.71131 | 0.70505 | 0.70075 | 0.69889 | 0.68648 | 0.68916 | 0.69697 | 0.71306 | 0.74672 | 0.80157 | 0.79561 | 0.79217 | 0.79205 | 0.79648 | 0.80202 | 0.82265 | 0.87191 | 0.83145 | 0.77828 | 0.75196 | 0.72653 | 0.70197 | 0.67823 | 0.65529 | 0.73213 | 0.71081 | 0.6901 | 0.67 | 0.65049 | 0.63154 | 0.61315 | 0.59529 | 0.57795 | 0.56112 | 0.54477 | 0.52891 | 0.5135 | 0.49855 | 0.48402 | 0.46993 | 0.45624 | 0.44295 | 0.43005 | 0.41752 | 0.40536 | 0.39356 | 0.38209 | 0.37096 | 0.36016 | 0.34967 | 0.33949 | 0.3296 | 0.32 | 0.31068 | 0.30163 | 0.29284 | 0.28431 | 0.27603 | 0.26799 | 0.26019 | 0.25261 | 0.24525 | 0.23811 | 0.23117 | 0.22444 | 0.2179 | 0.21156 | 0.20539 | 0.19941 | 0.27888 | 0.27208 | 0.26544 | 0.25897 | 0.25265
[19 empty] | Customer willingness to pay | Input | £000s
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 841.3695 | 853.5133 | 873.1707 | 899.8952 | 933.7979 | 1242.7474 | 1529.2842 | 1837.3491 | 2171.4461 | 2537.7693 | 2889.8958 | 3296.2017 | 3767.5898 | 4339.885 | 5108.7553 | 6119.0004 | 6688.8426 | 7339.9179 | 8097.2883 | 9001.125 | 10062.9816 | 11471.1276 | 13704.0255 | 15027.4678 | 14983.776 | 14983.7496 | 14983.7242 | 14983.6996 | 14983.6759 | 14983.653 | 14983.7298 | 14983.7085 | 14983.6878 | 14983.6677 | 14983.6482 | 14983.6292 | 14983.6108 | 14983.593 | 14983.5756 | 14983.5588 | 14983.5424 | 14983.5266 | 14983.5112 | 14983.4962 | 14983.4817 | 14983.4676 | 14983.4539 | 14983.4406 | 14983.4277 | 14983.4152 | 14983.403 | 14983.3912 | 14983.3798 | 14983.3686 | 14983.3578 | 14983.3473 | 14983.3372 | 14983.3273 | 14983.3177 | 14983.3083 | 14983.2993 | 14983.2905 | 14983.282 | 14983.2737 | 14983.2657 | 14983.2579 | 14983.2503 | 14983.2429 | 14983.2358 | 14983.2288 | 14983.2221 | 14983.2156 | 14983.2092 | 14983.2031 | 14983.1971 | 14983.2765 | 14983.2697 | 14983.2631 | 14983.2566 | 14983.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59.2a | Options to reduce Distribution System Operating Use (DSOU) losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60a | PRODUCTION SIDE | bar: 1 Year 1 to 80 Year 80
60.1a | Options to reduce treatment works losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60.2a | Options to reduce outage | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61a | CUSTOMER SIDE | bar: 1 Year 1 to 80 Year 80
61.1a | Options to change volume delivered to measured non households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.2a | Options to change volume delivered to unmeasured non households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.3a | Options to change volume delivered to measured households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Home water efficiency audits | WE001 | Retrofitting indoor water efficiency devices | Y | 2020-21 | Capacity | 9.5178 | 21686.0142 | 9412.4049 | 0 | -2844.1287 | 3741.2665 | 0 | 10309.5426 | 30.2881 | 47.5401 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.50606 | 1.0401 | 1.639 | 2.0421 | 2.6219 | 3.3073 | 4.1775 | 4.9969 | 5.7684 | 6.4948 | 7.1789 | 7.8188 | 8.2431 | 8.8334 | 9.3245 | 9.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| This is a company wide decision, and the AIC reflects the company wide costs and demand benefits for measured and unmeasured water efficiency programmes | [17 empty] | Fixed capex | Input | £000s | 879.7305 | 906.12 | 775.5 | 852.4787 | 775.5 | 775.5 | 775.5 | 775.5 | 775.5 | 775.5 | 775.5 | 765.7906 | 503.6798 | 772.1474 | 630.403 | 245.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Financing costs | Input | £000s
[12 empty] | 0 | [6 empty] | Fixed opex | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Variable opex | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Opex savings | Input | £000s | 24.2249 | 49.7889 | 78.4583 | 97.7572 | 125.5097 | 158.3215 | 199.9744 | 239.1996 | 276.133 | 310.9031 | 343.6511 | 374.2849 | 394.5956 | 422.8543 | 446.3606 | 455.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Variable env & social | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Fixed carbon costs | Input | £000s | 1.454 | 1.454 | 1.454 | 1.454 | 1.454 | 1.3078 | 1.3078 | 1.3078 | 1.3078 | 1.3078 | 0.4195 | 0.4195 | 0.4195 | 0.4195 | 0.4195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 406.6361 | 406.6361 | 406.6361 | 406.6361 | 406.6361 | 365.737 | 365.737 | 365.737 | 365.737 | 365.737 | 117.3202 | 117.3202 | 117.3202 | 117.3202 | 117.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 81 Year 81: 0; 82 Year 82: 0; 83 Year 83: 0; 84 Year 84: 0; 85 Year 85: 0; 86 Year 86: 0; 87 Year 87: 0; 88 Year 88: 0; 89 Year 89: 0; 90 Year 90: 0; 91 Year 91: 0; 92 Year 92: 0; 93 Year 93: 0; 94 Year 94: 0; 95 Year 95: 0; 96 Year 96: 0; 97 Year 97: 0; 98 Year 98: 0; 99 Year 99: 0; 100 Year 100: 0; 101 Year 101: 0; 102 Year 102: 0; 103 Year 103: 0; 104 Year 104: 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 1312.0456 | 1363.999 | 1262.0484 | 1358.326 | 1309.0999 | 1300.8662 | 1342.5191 | 1381.7443 | 1418.6778 | 1453.4478 | 1236.8908 | 1257.8152 | 1016.0152 | 1312.7414 | 1194.5033 | 701.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.4a | Options to change volume delivered to unmeasured households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Enhanced Metering | EM001 | Metering other selective | Y | 2020-21 | Capacity | 41.54 | 260373.7353 | 439070.7084 | 328248.2635 | -30851.6277 | 11101.6008 | 185038.0241 | 932606.9691 | 282.8501 | 358.1801 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 1.51 | 3.54 | 5.74 | 8.29 | 11.37 | 15.38 | 19.56 | 23.95 | 28.2 | 32.15 | 36.75 | 39.71 | 41.54 | 41.39 | 40.01 | 38.4 | 36.85 | 35.36 | 33.88 | 32.42 | 30.98 | 29.61 | 28.26 | 26.93 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 25.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| This is a company wide decision, and the AIC reflects the company wide costs and demand benefits | [17 empty] | Fixed capex | Input | £000s | 9026.9182 | 12461.6058 | 14080.5498 | 16727.1383 | 21293.654 | 25773.6826 | 26309.1372 | 28939.3516 | 29699.7874 | 30103.8717 | 36925.224 | 27676.4247 | 19952.7624 | 15944.2652 | 5189.7767 | 6281.6677 | 6412.1709 | 7053.2176 | 7238.5541 | 7337.0392 | 13391.5289 | 12808.4884 | 11713.7277 | 12024.4329 | 11625.0999 | 14070.9357 | 14363.2628 | 15799.2073 | 16214.3611 | 16434.9677 | 21157.9932 | 16488.7846 | 12451.2733 | 10555.7507 | 5189.7767 | 6281.6677 | 6412.1709 | 7053.2176 | 7238.5541 | 7337.0392 | 13391.5289 | 12808.4884 | 11713.7277 | 12024.4329 | 11625.0999 | 14070.9357 | 14363.2628 | 15799.2073 | 16214.3611 | 16434.9677 | 21157.9932 | 16488.7846 | 12451.2733 | 10555.7507 | 5189.7767 | 6281.6677 | 6412.1709 | 7053.2176 | 7238.5541 | 7337.0392 | 13391.5289 | 12808.4884 | 11713.7277 | 12024.4329 | 11625.0999 | 14070.9357 | 14363.2628 | 15799.2073 | 16214.3611 | 16434.9677 | 21157.9932 | 16488.7846 | 12451.2733 | 10555.7507 | 5189.7767 | 6281.6677 | 6412.1709 | 7053.2176 | 7238.5541 | 7337.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 440.0155 | 1047.4543 | 1733.8081 | 2549.1695 | 3587.1248 | 4843.4584 | 6125.8926 | 7536.5361 | 8984.2469 | 10451.6547 | 12144.3258 | 13345.3607 | 14150.6735 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 14729.1506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 41.2634 | 96.7366 | 156.7524 | 226.1633 | 329.6961 | 506.5882 | 756.9333 | 1036.2784 | 1289.7335 | 1486.8235 | 1666.9931 | 1774.5092 | 1835.9327 | 1818.4685 | 1757.8706 | 1687.0088 | 1619.3199 | 1553.9397 | 1489.4924 | 1424.4339 | 1361.9009 | 1302.561 | 1242.4513 | 1184.9365 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 1133.9368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 4360.9937 | 6020.3254 | 6802.4533 | 8081.0465 | 10287.1755 | 12451.5217 | 12710.2051 | 13980.8878 | 14348.2619 | 14543.479 | 16776.0627 | 11903.4569 | 7981.4556 | 5733.2869 | 0 | 0 | 0 | 0 | 0 | 0 | 2813.4592 | 3883.9633 | 4388.5467 | 5213.4205 | 6636.6865 | 8032.9967 | 8199.8841 | 9019.6546 | 9256.663 | 9382.6057 | 10822.9386 | 7679.4172 | 5149.1703 | 3698.7828 | 0 | 0 | 0 | 0 | 0 | 0 | 2813.4592 | 3883.9633 | 4388.5467 | 5213.4205 | 6636.6865 | 8032.9967 | 8199.8841 | 9019.6546 | 9256.663 | 9382.6057 | 10822.9386 | 7679.4172 | 5149.1703 | 3698.7828 | 0 | 0 | 0 | 0 | 0 | 0 | 2813.4592 | 3883.9633 | 4388.5467 | 5213.4205 | 6636.6865 | 8032.9967 | 8199.8841 | 9019.6546 | 9256.663 | 9382.6057 | 10822.9386 | 7679.4172 | 5149.1703 | 3698.7828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 264.7566 | 365.4949 | 412.978 | 490.6016 | 624.5361 | 755.9339 | 771.6386 | 848.7819 | 871.0853 | 882.9369 | 1018.4775 | 722.6608 | 484.5555 | 348.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 167.1357 | 230.7298 | 260.7049 | 309.7072 | 394.2574 | 477.2062 | 487.1203 | 535.8194 | 549.8991 | 557.3808 | 642.9448 | 456.2016 | 305.8904 | 219.729 | 0 | 0 | 0 | 0 | 0 | 0 | 167.1357 | 230.7298 | 260.7049 | 309.7072 | 394.2574 | 477.2062 | 487.1203 | 535.8194 | 549.8991 | 557.3808 | 642.9448 | 456.2016 | 305.8904 | 219.729 | 0 | 0 | 0 | 0 | 0 | 0 | 167.1357 | 230.7298 | 260.7049 | 309.7072 | 394.2574 | 477.2062 | 487.1203 | 535.8194 | 549.8991 | 557.3808 | 642.9448 | 456.2016 | 305.8904 | 219.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 14133.9474 | 19992.617 | 23188.5417 | 28077.1192 | 36126.1865 | 44336.1848 | 46679.8067 | 52348.8359 | 55201.115 | 57477.7659 | 68541.083 | 55433.4123 | 44417.3798 | 38586.24 | 21690.798 | 22712.8271 | 22776.6415 | 23353.3079 | 23475.1972 | 23509.6237 | 32483.1753 | 32975.8931 | 32356.5813 | 33484.6478 | 34543.1312 | 38469.226 | 38939.3547 | 41244.7688 | 41912.0106 | 42267.0416 | 48516.9641 | 40518.4908 | 33801.4214 | 30370.3499 | 21086.8642 | 22179.7551 | 22311.2583 | 22953.305 | 23139.6415 | 23239.1266 | 32275.2112 | 32827.269 | 32268.0668 | 33453.6481 | 34563.1312 | 38489.226 | 38959.3547 | 41264.7688 | 41932.0106 | 42287.0416 | 48536.9641 | 40538.4908 | 33821.4214 | 30390.3499 | 21106.8642 | 22199.7551 | 22331.2583 | 22973.305 | 23159.6415 | 23259.1266 | 32295.2112 | 32847.269 | 32288.0668 | 33473.6481 | 34583.1312 | 38509.226 | 38979.3547 | 41284.7688 | 41952.0106 | 42307.0416 | 48556.9641 | 40558.4908 | 33841.4214 | 30410.3499 | 21126.8642 | 22219.7551 | 22351.2583 | 22993.305 | 23179.6415 | 23279.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.5a | Options to reduce water taken unbilled | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.6a | Options impacting on measured Non Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.7a | Options impacting on unmeasured Non Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.8a | Options impacting on measured Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.9a | Options impacting on unmeasured Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Enhanced Metering | EM001 | Metering other selective | Y | 2020-21 | Capacity | 3.1036 | 24424.3228 | 32540.7368 | 27932.6092 | -3181.6271 | 441.8786 | 19235.4332 | 76969.0307 | 234.5683 | 315.1327 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.11209 | 0.26496 | 0.43539 | 0.63586 | 0.87186 | 0.74608 | 1.0158 | 1.3619 | 1.676 | 1.9984 | 2.619 | 2.8846 | 3.0446 | 3.1036 | 3.0862 | 3.0745 | 3.0631 | 3.0521 | 3.0414 | 3.0311 | 3.0212 | 3.0115 | 3.0022 | 2.9932 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 2.9844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| This is a company wide decision, and the AIC reflects the company wide costs and demand benefits | [17 empty] | Fixed capex | Input | £000s | 456.0506 | 629.5752 | 636.6518 | 646.0003 | 1008.2386 | 2426.7119 | 1954.7485 | 2216.6715 | 2370.8476 | 2622.496 | 3396.6618 | 1972.9778 | 1322.9127 | 950.2826 | 0 | 118.9238 | 164.1735 | 166.0189 | 168.4567 | 262.9172 | 879.4674 | 850.2455 | 922.3743 | 967.6347 | 1229.1747 | 2198.2397 | 1571.7241 | 1543.8695 | 1530.0859 | 1418.3869 | 1956.0212 | 1231.266 | 881.5212 | 682.4206 | 262.9172 | 632.8107 | 509.7374 | 578.0387 | 618.2431 | 683.8651 | 1132.4001 | 854.9991 | 689.3099 | 597.1957 | 545.3096 | 1431.4201 | 1221.4066 | 1364.9141 | 1450.7386 | 1681.304 | 2469.9081 | 1576.8299 | 1293.5411 | 1132.207 | 683.8651 | 885.7434 | 514.491 | 344.9743 | 247.804 | 0 | 365.5805 | 504.6816 | 510.3544 | 517.8484 | 808.2268 | 1945.307 | 1566.9705 | 1776.9339 | 1900.525 | 2102.2519 | 2722.8408 | 1581.5835 | 1060.4767 | 761.7679 | 0 | 118.9238 | 164.1735 | 166.0189 | 168.4567 | 262.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable capex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Financing costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed opex | Input | £000s | 10.6424 | 45.8585 | 90.6175 | 138.5505 | 190.2813 | 224.1065 | 359.8673 | 481.4673 | 611.9054 | 750.1349 | 928.1011 | 1107.5069 | 1212.2583 | 1277.9096 | 1319.3941 | 1318.2778 | 1317.1973 | 1316.1514 | 1315.139 | 1314.1622 | 1313.2167 | 1312.3015 | 1311.4156 | 1310.5581 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 1309.7313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable opex | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Opex savings | Input | £000s | 3.0631 | 7.2406 | 14.1561 | 25.6154 | 38.1358 | 28.179 | 45.6541 | 66.4173 | 84.469 | 98.7841 | 135.3593 | 144.8853 | 150.3589 | 151.957 | 150.6298 | 149.5429 | 148.4909 | 147.4726 | 146.4869 | 145.5358 | 144.6153 | 143.7243 | 142.8617 | 142.0269 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 141.2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed env & social | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable env & social | Input | £000s | 365.3709 | 505.8322 | 501.2014 | 490.4115 | 766.0016 | 1837.1893 | 1521.124 | 1730.4865 | 1851.3685 | 2070.9453 | 2663.621 | 1550.85 | 1054.367 | 769.3464 | 40.3001 | 40.1465 | 39.9979 | 39.854 | 39.7147 | 39.5803 | 182.1588 | 236.3326 | 233.5458 | 228.2316 | 335.0335 | 755.6185 | 630.2829 | 710.5896 | 756.3815 | 840.838 | 1070.081 | 632.3503 | 436.8411 | 324.7713 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 181.6792 | 235.979 | 233.314 | 228.1178 | 335.0335 | 755.6185 | 630.2829 | 710.5896 | 756.3815 | 840.838 | 1070.081 | 632.3503 | 436.8411 | 324.7713 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 181.6792 | 235.979 | 233.314 | 228.1178 | 335.0335 | 755.6185 | 630.2829 | 710.5896 | 756.3815 | 840.838 | 1070.081 | 632.3503 | 436.8411 | 324.7713 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 38.9707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Fixed carbon costs | Input | £000s | 8.6436 | 11.5792 | 11.8285 | 12.3844 | 20.8836 | 67.8135 | 46.4416 | 51.2174 | 52.4355 | 66.7498 | 63.7598 | 39.2088 | 25.7823 | 18.198 | 0.98936 | 0.95259 | 0.91728 | 0.88336 | 0.85078 | 0.81949 | 1.8688 | 2.2002 | 2.2497 | 2.3692 | 3.7555 | 12.3679 | 8.4346 | 9.2197 | 9.3391 | 12.5096 | 12.2971 | 8.0542 | 5.4419 | 3.9602 | 0.56863 | 0.55206 | 0.53599 | 0.52037 | 0.50522 | 0.4905 | 1.1346 | 1.3448 | 1.3832 | 1.4652 | 2.3356 | 7.7291 | 5.2966 | 5.8178 | 5.9217 | 7.9706 | 6.8086 | 4.4594 | 3.0131 | 2.1927 | 0.31483 | 0.30566 | 0.29676 | 0.28812 | 0.27973 | 0.27158 | 0.6282 | 0.74457 | 0.76586 | 0.81124 | 1.2932 | 4.2794 | 2.9326 | 3.2212 | 3.2787 | 4.4131 | 3.7698 | 2.4691 | 1.6683 | 1.214 | 0.17432 | 0.24378 | 0.23784 | 0.23204 | 0.22638 | 0.22086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Variable carbon costs | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Customer willingness to pay | Input | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 843.7707 | 1200.0856 | 1254.4553 | 1312.962 | 2023.5408 | 4584.0003 | 3927.8355 | 4546.26 | 4971.026 | 5609.1101 | 7187.5031 | 4815.4288 | 3765.6792 | 3167.6935 | 1511.3134 | 1627.8437 | 1670.7769 | 1670.3802 | 1670.648 | 1763.015 | 2521.327 | 2544.804 | 2612.4471 | 2650.8205 | 3018.917 | 4417.1792 | 3661.3948 | 3714.632 | 3746.7597 | 3722.6876 | 4489.3525 | 3322.6237 | 2774.7575 | 2462.1053 | 1753.4097 | 2123.2867 | 2000.1973 | 2068.483 | 2108.6722 | 2174.2795 | 2766.1671 | 2543.276 | 2374.9603 | 2277.7319 | 2333.632 | 3645.7208 | 3307.9394 | 3532.2746 | 3663.995 | 3981.0658 | 4997.7509 | 3664.5928 | 3184.3484 | 2910.1242 | 2174.1038 | 2375.9729 | 2004.7117 | 1835.1864 | 1738.0077 | 1490.1955 | 1998.8411 | 2192.3584 | 2195.3875 | 2197.7306 | 2595.5067 | 4156.1581 | 3651.1392 | 3941.6978 | 4111.1383 | 4398.4562 | 5247.6447 | 3667.3561 | 2949.9392 | 2538.7065 | 1490.0982 | 1609.0915 | 1654.3353 | 1656.1748 | 1658.607 | 1753.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.10a | Options impacting on Void properties - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RZCOSTSHERE
| Company: | Severn Trent Water
| Resource Zone Name: | North Staffordshire
| Resource Zone Number: | 7
| Planning Scenario Name: | Dry Year Annual Average
| Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans
Start dates | Option Categories
2020-21 | Aquifer recharge
2021-22 | Bulk supply
2022-23 | Conjunctive use
2023-24 | Desalination
2024-25 | Effluent reuse
2025-26 | GW enhancement
2026-27 | GW new
2027-28 | Reservoir enlargement
2028-29 | New reservoir
2029-30 | SW enhancement
2030-31 | SW new
2031-32
2032-33
2033-34 | Active leakage management
2034-35 | Mains repair
2035-36 | Mains replacement (not trunk mains)
2036-37 | Pressure management
2037-38 | Other leakage control
2038-39 | Trunk mains renewal
2039-40 | Pumps
2040-41 | Service reservoir
2041-42
2042-43
2043-44 | Water treatment works loss recovery
2044-45 | Water treatment works capacity increase
Cistern displacement device
Household water audit
Commercial water audit
Customer education / awareness
Other water efficiency
Metering optants
Metering change of occupancy
Metering compulsory
Metering other selective
Supply pipe repairs / replacement
Outdoor water efficiency devices
Retrofitting indoor water efficiency devices
Alternative tariffs
Collaborative R&D
Note on DW1: Author: At year 126 this drops to 2%
Note on V2: The original formulae assumed 80 whatever number was put here. The formulae in this sheet will take account of the number.
Note on X2: Cells X2:CY2 contain a factor to calculate NPV based on variable discount rate - please do not adjust
Note on CY2: Formula can be copied across to the right if appraisal period extends beyond 80 years

## 6. Preferred (Scenario Yr)
Table 6: Preferred list of water management options
DRY YEAR PLANNED GAINS IN WAFU OR SAVINGS IN DEMAND (Ml/d) - TO BE COMPLETED FOR ALL PREFERRED OPTIONS (WAFU gains for each year are individual year gains and not cumulative gains)
Row Ref | Option Name [Insert / delete non-numbered lines to suit] | Option Reference No. | Unit | Decimal places | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | Comments | 1st line | Initials
58 | Resource Management | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
58.1 | Increase raw water abstractions | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
- | Peckforton Group BHs asset and water treatment enhancements | GRD18 | Ml/d | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | Moved from 2025 to 2026/27 completion date at SOR. (S27). This seams to be incorrect. The data in the "Scenario Calc S23-27" show that date 2026 (Should be linked to the 25/26 year) | 2018-12-18 | JG
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.2 | Raw water imports | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.3 | Potable water Imports (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.4 | Reduce raw water losses and operational use (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.5 | Reduced raw water export (including non potable supplies) |  | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.51 | Reduce raw water exports (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.52 | Reduce non potable supplies (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.6 | Reduce potable water exports (input as -ve) | - | Ml/d |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.7 | Other options to increase deployable output | - | Ml/d |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5
- | Improve Tittesworth WTW outputs during low raw water periods | UNK07 | Ml/d | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
| This line has been added to show the overall zonal benefit found from including scheme GRD18. This is because the effect of WINEP 2 on the peckforton Control group was to split the overall NS zone. This scheme keeps the zone together and therefore reduces the zonal DO drop by this value. | [7 empty] | 0 | 0 | 0 | 0 | 0 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | Moved from 2025 to 2026/27 completion date at SOR. (S27). This seams to be incorrect. The data in the "Scenario Calc S23-27" show that date 2026 (Should be linked to the 25/26 year) | 2018-12-18 | JG
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
59 | Distribution Side Management | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.8323 | -1.7146 | -2.5969 | -3.4792 | -4.3615 | -5.1115 | -5.8614 | -6.6114 | -7.3613 | -8.1113 | -8.5362 | -8.9612 | -9.3862 | -9.8112 | -10.2361 | -10.6186 | -11.0011 | -11.3836 | -11.7661 | -12.1485
59.1 | Reduce distribution losses (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.8323 | -1.7146 | -2.5969 | -3.4792 | -4.3615 | -5.1115 | -5.8614 | -6.6114 | -7.3613 | -8.1113 | -8.5362 | -8.9612 | -9.3862 | -9.8112 | -10.2361 | -10.6186 | -11.0011 | -11.3836 | -11.7661 | -12.1485
| Leakage Reduction | ALC2 | Ml/d | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | -0.8323 | -1.7146 | -2.5969 | -3.4792 | -4.3615 | -5.1115 | -5.8614 | -6.6114 | -7.3613 | -8.1113 | -8.5362 | -8.9612 | -9.3862 | -9.8112 | -10.2361 | -10.6186 | -11.0011 | -11.3836 | -11.7661 | -12.1485
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
59.2 | Reduce distribution system operational use (DSOU) (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
60 | Production Side Management, Specify Below.... | - |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60.1 | Reduce treatment works losses (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
60.2 | Reduce outages (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61 | Customer Side Management | - |  | 2 | 0 | 0 | 0 | 0 | -0.1437 | -0.31013 | -0.90772 | -2.4962 | -4.0844 | -3.7029 | -3.4921 | -3.2736 | -3.0758 | -2.8908 | -2.761 | -2.6409 | -2.4967 | -2.3774 | -2.2584 | -2.1484 | -2.029 | -1.9288 | -1.8195 | -1.7195 | -1.6106 | -1.4113 | -1.2065 | -1.1107 | -1.2696
61.1 | Change volume delivered to measured non households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.2 | Change volume delivered to unmeasured non households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.3 | Change volume delivered to measured households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.1437 | -0.31013 | 4.8153 | 18.3105 | 32.1282 | 31.5443 | 31.028 | 30.538 | 30.0503 | 29.5627 | 29.0226 | 28.4793 | 27.968 | 27.448 | 26.9408 | 26.4656 | 26.0149 | 25.5574 | 25.1181 | 24.6827 | 24.2672 | 23.9531 | 23.6567 | 23.2619 | 22.5861
| Home water efficiency checks | WE001 | Ml/d | 2 |  |  |  |  | -0.1437 | -0.31013 | -0.30475 | -0.29945 | -0.29425 | -0.28914 | -0.20911 | -0.13048 | -0.053215 | 0.01155 | 0.011349 | 0.011152 | 0.034748 | 0.034145 | 0.033552 | 0.032969 | 0.032396 | 0.031833 | 0.03128 | 0.030737 | 0.030203 | 0.12913 | 0.2438 | 0.23957 | 0
| Enhanced metering | EM001 | Ml/d | 2 |  |  |  |  | 0 | 0 | 5.12 | 18.61 | 32.4224 | 31.8334 | 31.2371 | 30.6685 | 30.1035 | 29.5511 | 29.0112 | 28.4682 | 27.9332 | 27.4139 | 26.9073 | 26.4326 | 25.9825 | 25.5256 | 25.0869 | 24.652 | 24.237 | 23.8239 | 23.4129 | 23.0223 | 22.5861
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.4 | Change volume delivered to unmeasured households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -5.68 | -20.65 | -35.946 | -35.1971 | -34.4701 | -33.7617 | -33.0761 | -32.4035 | -31.7336 | -31.0702 | -30.4147 | -29.7754 | -29.1492 | -28.564 | -27.9939 | -27.4362 | -26.8876 | -26.3522 | -25.8278 | -25.3144 | -24.8133 | -24.3226 | -23.8057
| Enhanced metering | EM001 | Ml/d | 2 |  |  |  |  | 0 | 0 | -5.68 | -20.65 | -35.946 | -35.1971 | -34.4701 | -33.7617 | -33.0761 | -32.4035 | -31.7336 | -31.0702 | -30.4147 | -29.7754 | -29.1492 | -28.564 | -27.9939 | -27.4362 | -26.8876 | -26.3522 | -25.8278 | -25.3144 | -24.8133 | -24.3226 | -23.8057
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.5 | Options to reduce water taken unbilled (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.6 | Options impacting on measured Non Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.7 | Options impacting on unmeasured Non Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.8 | Options impacting on measured Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41198 | 1.5031 | 2.6432 | 2.8064 | 2.754 | 2.7026 | 2.6521 | 2.6026 | 2.5539 | 2.5061 | 2.4592 | 2.4131 | 2.3679 | 2.3235 | 2.2799 | 2.237 | 2.195 | 2.1536 | 2.1131 | 2.0732 | 2.0341 | 1.9957 | 1.9579
- | Enhanced metering | EM001 | Ml/d | 2 |  |  |  |  | 0 | 0 | 0.41198 | 1.5031 | 2.6432 | 2.8064 | 2.754 | 2.7026 | 2.6521 | 2.6026 | 2.5539 | 2.5061 | 2.4592 | 2.4131 | 2.3679 | 2.3235 | 2.2799 | 2.237 | 2.195 | 2.1536 | 2.1131 | 2.0732 | 2.0341 | 1.9957 | 1.9579
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.9 | Options impacting on unmeasured Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -0.45495 | -1.6598 | -2.9097 | -2.8564 | -2.804 | -2.7526 | -2.7021 | -2.6526 | -2.6039 | -2.5561 | -2.5092 | -2.4631 | -2.4179 | -2.3735 | -2.3299 | -2.287 | -2.245 | -2.2036 | -2.1631 | -2.1232 | -2.0841 | -2.0457 | -2.0079
- | Enhanced metering | EM001 | Ml/d | 2 |  |  |  |  | 0 | 0 | -0.45495 | -1.6598 | -2.9097 | -2.8564 | -2.804 | -2.7526 | -2.7021 | -2.6526 | -2.6039 | -2.5561 | -2.5092 | -2.4631 | -2.4179 | -2.3735 | -2.3299 | -2.287 | -2.245 | -2.2036 | -2.1631 | -2.1232 | -2.0841 | -2.0457 | -2.0079
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.1 | Options impacting on Void properties - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
| Company: | Severn Trent Water
| Resource Zone Name: | North Staffordshire
| Resource Zone Number: | 7
| Planning Scenario Name: | Dry Year Annual Average
| Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans

## 7. FP Supply
Table 7: Final planning water supply
| Row Ref | Component | Derivation | Unit | Decimal places | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
Resources | 1FP | Raw Water Abstracted | 1BL | Ml/d | 2 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629 | 135.2629
| 2FP | Raw Water Imported | 2BL+ (6. Preferred scenario ref 58.2) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| 3FP | Potable Water Imported | 3BL+ (6. Preferred scenario ref 58.3) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
Resource (and process) losses | 5FP | Raw Water Exported (raw exports and non potable uses) | 5BL+ (6. Preferred scenario ref 58.5) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| 6FP | Potable Water Exported | 6BL+ (6. Preferred scenario ref 58.6) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| 7FP | Deployable Output | 7BL+ 8BL+ (6. Preferred scenario ref 58.7) + (6. Preferred scenario ref 58.1) |  | 2 | 132.9571 | 132.9571 | 132.9571 | 132.9571 | 131.3571 | 130.9571 | 130.5571 | 130.1571 | 129.7571 | 129.3571 | 128.9571 | 128.5571 | 128.1571 | 127.7571 | 127.4571 | 127.3571 | 127.2571 | 127.1571 | 127.0571 | 133.9571 | 133.8571 | 133.7571 | 133.6571 | 133.5571 | 133.4571 | 133.3571 | 133.2571 | 133.1571 | 133.0571
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2044-45
| 9FP | Raw water losses, treatment works losses and operational use | 9BL+ (6. Preferred scenario ref 60.1) +(6. Preferred scenario ref 58.4) | Ml/d | 2 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039 | 2.3039
| 10FP | Outage allowance | 10BL+ (6. Preferred scenario ref 60.2) | Ml/d | 2 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69
|  | Company: | Severn Trent Water
|  | Resource Zone Name: | North Staffordshire
|  | Resource Zone Number: | 7
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans

## 8. FP Demand
Table 8: Final planning water demand
| Row Ref | Component | Derivation / Impact of preferred options | Unit | Decimal places | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
Consumption | 19FP | Water Delivered Measured Non Household | Calculated BL+Preferred options | Ml/d | 2 | 21.8159 | 21.8406 | 21.8257 | 21.8519 | 21.8324 | 21.9449 | 22.0173 | 22.0861 | 22.077 | 22.1599 | 22.179 | 22.1977 | 22.1565 | 22.233 | 22.2548 | 22.278 | 22.2394 | 22.3165 | 22.3311 | 22.345 | 22.2973 | 22.3736 | 22.3918 | 22.4109 | 22.3706 | 22.4517 | 22.4734 | 22.4957 | 22.4584
| 20FP | Water Delivered Unmeasured Non Household | Calculated BL+Preferred options | Ml/d | 2 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738 | 0.41738
| 21FP | Water Delivered Measured Household | Calculated BL+Preferred options | Ml/d | 2 | 26.6642 | 27.4889 | 28.2978 | 29.1256 | 29.7403 | 30.3528 | 36.6772 | 52.0423 | 67.781 | 68.1372 | 68.3386 | 68.562 | 68.7874 | 69.0022 | 69.0307 | 69.0552 | 69.0868 | 69.0985 | 69.1077 | 69.187 | 69.2854 | 69.3671 | 69.451 | 69.5318 | 69.6218 | 69.8055 | 70.0014 | 70.0895 | 69.9301
| 22FP | Water Delivered Unmeasured Household | Calculated BL+Preferred options | Ml/d | 2 | 46.2133 | 45.2152 | 44.2273 | 43.2788 | 42.3167 | 41.4077 | 34.3967 | 17.3692 | -4.885e-15 | -3.5527e-15 | 0 | 4.885e-15 | 0 | -6.2172e-15 | 0 | 0 | 0 | -3.5527e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23FP | Measured Non Household - Consumption | 19FP-34FP | Ml/d | 2 | 21.386 | 21.4107 | 21.3958 | 21.422 | 21.4025 | 21.515 | 21.5873 | 21.6562 | 21.6471 | 21.7299 | 21.7491 | 21.7678 | 21.7266 | 21.8031 | 21.8249 | 21.8481 | 21.8095 | 21.8866 | 21.9012 | 21.9151 | 21.8674 | 21.9437 | 21.9619 | 21.981 | 21.9407 | 22.0217 | 22.0435 | 22.0658 | 22.0285
| 24FP | Unmeasured Non Household - Consumption | 20FP-35FP | Ml/d | 2 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433 | 0.40433
| 25FP | Measured Household - Consumption | 21FP-36FP | Ml/d | 2 | 24.129 | 24.9018 | 25.6586 | 26.4346 | 26.9994 | 27.5631 | 33.4277 | 47.6547 | 62.2073 | 62.3551 | 62.5646 | 62.796 | 63.0294 | 63.252 | 63.2883 | 63.3204 | 63.3596 | 63.3788 | 63.3954 | 63.482 | 63.5878 | 63.6766 | 63.7676 | 63.8555 | 63.9525 | 64.1412 | 64.342 | 64.4349 | 64.2802
| 26FP | Unmeasured Household - Consumption | 22FP-37FP | Ml/d | 2 | 42.8391 | 41.9019 | 40.9749 | 40.0872 | 39.1836 | 38.332 | 31.8323 | 16.065 | -4.885e-15 | -3.5527e-15 | 0 | 4.885e-15 | 0 | -6.2172e-15 | 0 | 0 | 0 | -3.5527e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 27 - | Percentage of consumption driven by climate change | n/a in FP | - | 1 | - | - | - | - | bar: 2020-21 to 2044-45
| 28 - | Volume of consumption driven by climate change | n/a in FP | - | 1 | - | - | - | - | bar: 2020-21 to 2044-45
PCC and consumption by component | 29FP | Measured Household - PCC | (25FP*1,000,000)/(51FP*1,000) | l/h/d | 1 | 112 | 111.5 | 111 | 110.7 | 109.7 | 108.8 | 110.7 | 113.7 | 115.5 | 115.4 | 115.4 | 115.5 | 115.6 | 115.6 | 115.4 | 115.1 | 114.9 | 114.7 | 114.5 | 114.4 | 114.3 | 114.2 | 114.2 | 114.1 | 114 | 114.1 | 114.2 | 114.1 | 113.6
| 29.1FP | Measured toilet flushing | Input brief explanation here | l/h/d | 1 | 25.4946 | 24.732 | 24.0154 | 23.3357 | 22.6896 | 22.071 | 21.9477 | 22.0854 | 21.8662 | 21.2284 | 20.5958 | 19.9694 | 19.3484 | 18.7343 | 18.7069 | 18.6813 | 18.6575 | 18.6335 | 18.6098 | 18.585 | 18.5602 | 18.5348 | 18.5097 | 18.4837 | 18.4575 | 18.4309 | 18.4041 | 18.3769 | 18.3493
| 29.2FP | Measured personal washing | Input brief explanation here | l/h/d | 1 | 47.1755 | 47.9983 | 48.825 | 49.6522 | 50.4822 | 51.3113 | 53.1215 | 55.5557 | 57.3192 | 58.1437 | 58.9652 | 59.788 | 60.6094 | 61.4352 | 61.4536 | 61.4779 | 61.5084 | 61.5381 | 61.5689 | 61.596 | 61.6227 | 61.6479 | 61.6738 | 61.6971 | 61.7193 | 61.7403 | 61.7605 | 61.7794 | 61.7971
| 29.3FP | Measured clothes washing | Input brief explanation here | l/h/d | 1 | 13.9195 | 13.8272 | 13.7401 | 13.6564 | 13.5759 | 13.4973 | 13.6615 | 13.9763 | 14.124 | 14.0432 | 13.9626 | 13.8832 | 13.8042 | 13.7271 | 13.6208 | 13.5157 | 13.4118 | 13.3077 | 13.2038 | 13.099 | 12.994 | 12.8886 | 12.7832 | 12.6773 | 12.5711 | 12.4645 | 12.3577 | 12.2506 | 12.1432
| 29.4FP | Measured dish washing | Input brief explanation here | l/h/d | 1 | 10.9572 | 10.9519 | 10.9479 | 10.9442 | 10.9413 | 10.9383 | 11.1353 | 11.4594 | 11.6468 | 11.6429 | 11.6385 | 11.6343 | 11.6299 | 11.6263 | 11.6203 | 11.6155 | 11.6118 | 11.608 | 11.6043 | 11.6 | 11.5956 | 11.5909 | 11.5863 | 11.5812 | 11.5759 | 11.5704 | 11.5647 | 11.5587 | 11.5526
| 29.5FP | Measured miscellaneous internal use | Input brief explanation here | l/h/d | 1 | 13.1684 | 13.0812 | 13.0033 | 12.932 | 12.8676 | 12.8079 | 12.6295 | 12.3978 | 12.2734 | 12.2721 | 12.2701 | 12.2685 | 12.2666 | 12.2656 | 12.2634 | 12.262 | 12.2619 | 12.2618 | 12.2619 | 12.2614 | 12.2608 | 12.2601 | 12.2595 | 12.2585 | 12.2573 | 12.256 | 12.2545 | 12.2529 | 12.2511
| 29.6FP | Measured external use | Input brief explanation here | l/h/d | 1 | 1.3034 | 1.3402 | 1.3769 | 1.4135 | 1.4498 | 1.486 | 1.5334 | 1.5896 | 1.639 | 1.6767 | 1.7142 | 1.7516 | 1.7889 | 1.8261 | 1.8621 | 1.8977 | 1.933 | 1.968 | 2.0027 | 2.0371 | 2.0711 | 2.1047 | 2.1381 | 2.1711 | 2.2038 | 2.2361 | 2.2682 | 2.2999 | 2.3313
| 29.7FP | Measured water efficiency savings | Input brief explanation here | l/h/d | 1 | -0.018667 | -0.43075 | -0.90852 | -1.234 | -2.3064 | -3.3116 | -3.3289 | -3.3642 | -3.3686 | -3.6069 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463 | -3.7463
| 30FP | Unmeasured Household - PCC | (26FP*1,000,000)/(52FP*1,000) | l/h/d | 1 | 138.4 | 138.1 | 137.8 | 137.5 | 137.2 | 136.9 | 136.7 | 136.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 30.1FP | Unmeasured toilet flushing | Input brief explanation here | l/h/d | 1 | 31.2067 | 30.4165 | 29.6282 | 28.8375 | 28.0494 | 27.2579 | 26.4648 | 25.6742 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 30.2FP | Unmeasured personal washing | Input brief explanation here | l/h/d | 1 | 57.8437 | 58.7166 | 59.596 | 60.4732 | 61.359 | 62.2405 | 63.1212 | 64.0113 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 30.3FP | Unmeasured clothes washing | Input brief explanation here | l/h/d | 1 | 16.6882 | 16.5959 | 16.5051 | 16.4133 | 16.3234 | 16.232 | 16.14 | 16.0501 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 30.4FP | Unmeasured dish washing | Input brief explanation here | l/h/d | 1 | 13.1993 | 13.1956 | 13.1932 | 13.19 | 13.1885 | 13.1859 | 13.1828 | 13.1815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 30.5FP | Unmeasured miscellaneous internal use | Input brief explanation here | l/h/d | 1 | 18.0701 | 18.0789 | 18.0895 | 18.0991 | 18.1109 | 18.1212 | 18.131 | 18.1432 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 30.6FP | Unmeasured external use | Input brief explanation here | l/h/d | 1 | 1.4393 | 1.4847 | 1.5302 | 1.5755 | 1.621 | 1.6662 | 1.7114 | 1.7567 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 30.7FP | Unmeasured water efficiency savings | Input brief explanation here | l/h/d | 1 | -0.047295 | -0.38824 | -0.74221 | -1.0886 | -1.4522 | -1.8038 | -2.0513 | -2.317 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| 31FP | Average Household - PCC | ((25FP+26FP)*1,000,000))/(51FP+52FP*1,000) | l/h/d | 1 | 127.6004 | 126.8047 | 126.0791 | 125.4797 | 124.4857 | 123.5676 | 121.9898 | 118.7256 | 115.5078 | 115.4066 | 115.4256 | 115.4946 | 115.5608 | 115.6412 | 115.3735 | 115.1141 | 114.923 | 114.6989 | 114.4892 | 114.3874 | 114.3265 | 114.2322 | 114.1574 | 114.0657 | 113.9922 | 114.0812 | 114.1943 | 114.1145 | 113.5975
| 32FP | Water Taken Unbilled | Calculated BL+Preferred options | Ml/d | 1 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.3134
| 33FP | Distribution System Operational Use | Calculated BL+Preferred options | Ml/d | 1 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721 | 0.33721
Leakage | 34FP | Measured Non Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992
| 35FP | Unmeasured Non Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305 | 0.01305
| 36FP | Measured Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 2.5352 | 2.5872 | 2.6391 | 2.6911 | 2.7409 | 2.7897 | 3.2495 | 4.3876 | 5.5737 | 5.7821 | 5.774 | 5.766 | 5.758 | 5.7502 | 5.7424 | 5.7348 | 5.7272 | 5.7197 | 5.7123 | 5.7049 | 5.6977 | 5.6905 | 5.6834 | 5.6763 | 5.6693 | 5.6644 | 5.6595 | 5.6547 | 5.65
| 37FP | Unmeasured Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 3.3742 | 3.3133 | 3.2524 | 3.1915 | 3.1331 | 3.0757 | 2.5644 | 1.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 38FP | Void Properties - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992 | 0.42992
| 39FP | Distribution Losses | Calculated BL+Preferred options | Ml/d | 2 | 23.0777 | 22.9367 | 22.7956 | 22.6545 | 22.6632 | 22.6718 | 22.6802 | 22.6886 | 22.6969 | 21.8727 | 20.9985 | 20.1243 | 19.2499 | 18.3754 | 17.6332 | 16.8909 | 16.1485 | 15.4061 | 14.6636 | 14.2459 | 13.8282 | 13.4104 | 12.9926 | 12.5746 | 12.1992 | 11.8216 | 11.4441 | 11.0664 | 10.6886
| 40FP | Total Leakage | Sum(34FP:39FP) | Ml/d | 2 | 29.86 | 29.71 | 29.56 | 29.41 | 29.41 | 29.41 | 29.367 | 29.2532 | 29.1435 | 28.5277 | 27.6454 | 26.7631 | 25.8808 | 24.9985 | 24.2485 | 23.4986 | 22.7486 | 21.9987 | 21.2487 | 20.8238 | 20.3988 | 19.9738 | 19.5488 | 19.1239 | 18.7414 | 18.3589 | 17.9764 | 17.5939 | 17.2115
| 41FP | Total Leakage | (40FP*1,000,000)/(48FP*1,000) | l/prop/d | 2 | 118.9865 | 117.5697 | 116.1995 | 114.8597 | 114.1149 | 113.3766 | 112.4731 | 111.3177 | 110.1941 | 107.1587 | 103.1786 | 99.2527 | 95.3842 | 91.5687 | 88.3026 | 85.0412 | 81.8202 | 78.6389 | 75.4965 | 73.5399 | 71.6061 | 69.6957 | 67.8081 | 65.9429 | 64.2454 | 62.5678 | 60.9098 | 59.271 | 57.6511
Customer: Properties | 42FP | Measured Non Household - Properties | Input (total, excluding voids) | 000's | 2 | 11.7713 | 11.8173 | 11.8633 | 11.9093 | 11.9553 | 12.0013 | 12.0473 | 12.0933 | 12.1393 | 12.1853 | 12.2313 | 12.2773 | 12.3233 | 12.3692 | 12.4152 | 12.4612 | 12.5071 | 12.5531 | 12.599 | 12.645 | 12.6909 | 12.7368 | 12.7828 | 12.8287 | 12.8746 | 12.9205 | 12.9664 | 13.0124 | 13.0583
| 43FP | Unmeasured Non Household - Properties | Input (total, excluding voids) | 000's | 2 | 0.49182 | 0.48371 | 0.47559 | 0.46747 | 0.45936 | 0.45124 | 0.44312 | 0.43501 | 0.42689 | 0.41877 | 0.41066 | 0.40254 | 0.39442 | 0.38631 | 0.37819 | 0.37007 | 0.36195 | 0.35384 | 0.34572 | 0.3376 | 0.32949 | 0.32137 | 0.31325 | 0.30514 | 0.29702 | 0.2889 | 0.28079 | 0.27267 | 0.26455
| 44FP | All void non-households - properties | Input (voids in each year) | 000's | 2 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993 | 3.4993
| 45FP | Measured Household - Properties (excl voids) | Pre-plan year = input. Forecast years = Previous year 45FP + sum(45.1FP:45.6FP) | 000's | 2 | 98.3805 | 102.3525 | 106.2614 | 110.1396 | 113.9363 | 117.6987 | 138.2949 | 186.5857 | 236.05 | 237.7571 | 239.4375 | 241.1082 | 242.7564 | 244.3892 | 245.956 | 247.6308 | 249.3048 | 250.978 | 252.6505 | 254.3223 | 255.9963 | 257.6697 | 259.3424 | 261.0145 | 262.6858 | 264.3565 | 266.0266 | 267.696 | 269.3648
| 45.1FP | New properties | Input (new builds in each year) | 000's | 2 | 1.8356 | 1.8316 | 1.77 | 1.7409 | 1.7487 | 1.7543 | 1.7758 | 1.7601 | 1.7544 | 1.7528 | 1.7254 | 1.7152 | 1.692 | 1.6761 | 1.6096 | 1.7168 | 1.7154 | 1.7141 | 1.7127 | 1.7115 | 1.7133 | 1.712 | 1.7108 | 1.7096 | 1.7085 | 1.7073 | 1.7062 | 1.7051 | 1.7041
| 45.2FP | Meter optants - properties | Input (meter optants in each year) | 000's | 2 | 2.245 | 2.1921 | 2.1897 | 2.1874 | 2.0973 | 2.0566 | 2.0167 | 1.6771 | 0.84419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.3FP | Compulsory metering - properties | Input (compulsory meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8516 | 44.9006 | 46.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.4FP | Metering on change of occupancy - properties | Input (change of occupancy meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.5FP | Selective metering properties | Input (selective meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.6FP | Other changes to existing metering - properties | Input (other changes to meters in each year) | 000's | 2 | 0 | -0.051627 | -0.050818 | -0.050047 | -0.049278 | -0.048523 | -0.04776 | -0.047055 | -0.046358 | -0.045671 | -0.045052 | -0.044423 | -0.043842 | -0.043268 | -0.042848 | -0.041979 | -0.041397 | -0.040826 | -0.040266 | -0.039719 | -0.039171 | -0.038645 | -0.038129 | -0.037623 | -0.037127 | -0.036641 | -0.036164 | -0.035697 | -0.035239
| 45.7FP | Measured void households - properties | Input (voids in each year) | 000's | 2 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 4.5217 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587 | 12.3587
| 46FP | Unmeasured households - properties (excl void) | Input (total) | 000's | 2 | 124.4512 | 122.1898 | 119.9318 | 117.6771 | 115.5136 | 113.3918 | 94.4594 | 47.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 47FP | Unmeasured void households - properties | Input (voids in each year) | 000's | 2 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 7.8369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 48FP | Total Resource Zone Properties (incl voids) | SUM(42FP:45FP)+45.7FP+46FP+47FP | 000's | 2 | 250.9527 | 252.7012 | 254.3901 | 256.0515 | 257.7226 | 259.401 | 261.1028 | 262.7905 | 264.4742 | 266.2192 | 267.9374 | 269.646 | 271.332 | 273.0027 | 274.6074 | 276.32 | 278.0319 | 279.7429 | 281.4532 | 283.1628 | 284.8747 | 286.5859 | 288.2964 | 290.0063 | 291.7154 | 293.4239 | 295.1318 | 296.839 | 298.5456
Customer: Population | 49FP | Measured Non Household - Population | Input (total) | 000's | 2 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064 | 10.064
| 50FP | Unmeasured Non Household - Population | Input (total) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 51FP | Measured Household - Population | Input (total) | 000's | 2 | 215.4017 | 223.382 | 231.0953 | 238.698 | 246.026 | 253.2827 | 302.0308 | 418.9738 | 538.555 | 540.3078 | 542.034 | 543.7139 | 545.422 | 546.9675 | 548.5514 | 550.0662 | 551.322 | 552.5665 | 553.7244 | 554.9736 | 556.1944 | 557.4312 | 558.5937 | 559.8131 | 561.025 | 562.2411 | 563.4427 | 564.6511 | 565.8588
| 52FP | Unmeasured Household - Population | Input (total) | 000's | 2 | 309.4255 | 303.4415 | 297.4106 | 291.4419 | 285.6263 | 279.9894 | 232.932 | 117.7233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 53FP | Total Resource Zone Population | 49FP+Sum(50FP:52FP) | 000's | 2 | 534.8912 | 536.8875 | 538.5699 | 540.2038 | 541.7162 | 543.3361 | 545.0268 | 546.7611 | 548.619 | 550.3718 | 552.098 | 553.7779 | 555.486 | 557.0315 | 558.6154 | 560.1302 | 561.386 | 562.6305 | 563.7884 | 565.0376 | 566.2584 | 567.4952 | 568.6577 | 569.8771 | 571.089 | 572.3051 | 573.5067 | 574.7151 | 575.9228
Occupancy | 54FP | Measured Household - Occupancy Rate (average) (excl voids) | 51FP/45FP | h/prop | 1 | 2.1895 | 2.1825 | 2.1748 | 2.1672 | 2.1593 | 2.152 | 2.184 | 2.2455 | 2.2815 | 2.2725 | 2.2638 | 2.2551 | 2.2468 | 2.2381 | 2.2303 | 2.2213 | 2.2114 | 2.2017 | 2.1917 | 2.1822 | 2.1727 | 2.1634 | 2.1539 | 2.1448 | 2.1357 | 2.1268 | 2.118 | 2.1093 | 2.1007
| 55FP | Unmeasured Household - Occupancy Rate | 52BL/46BL | h/prop | 1 | 2.4863 | 2.4834 | 2.4798 | 2.4766 | 2.4727 | 2.4692 | 2.4659 | 2.4619 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Metering | 56FP | Total Household Metering penetration (excl. voids) | 45FP/45FP+46FP | % | 0 | 44.15% | 45.58% | 46.98% | 48.35% | 49.66% | 50.93% | 59.42% | 79.6% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| 57FP | Total Household Metering penetration (incl. voids) | 45FP/(45FP+45.7FP+46FP+47FP) | % | 0 | 41.83% | 43.2% | 44.54% | 45.86% | 47.12% | 48.35% | 56.42% | 75.61% | 95.02% | 95.06% | 95.09% | 95.12% | 95.16% | 95.19% | 95.22% | 95.25% | 95.28% | 95.31% | 95.34% | 95.37% | 95.39% | 95.42% | 95.45% | 95.48% | 95.51% | 95.53% | 95.56% | 95.59% | 95.61%
|  | Company: | Severn Trent Water
|  | Resource Zone Name: | North Staffordshire
|  | Resource Zone Number: | 7
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans
Note on P21: STW: 100% metering
Note on P60: STW: 100% metering

## 9. FP SDB
Table 9: Final planning water supply
| Row Ref | Component | Derivation | Unit | Decimal places | 2016-17 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
SDB | 11FP | Distribution Input | 19FP+20FP+21FP+22FP+32FP+33FP+38FP+39FP | Ml/d | 2 | 122.2691 | 121.9794 | 121.6443 | 121.4087 | 121.0505 | 120.8751 | 120.2694 | 118.6841 | 117.0528 | 116.6677 | 116.0141 | 115.3819 | 114.6918 | 114.1085 | 113.4167 | 112.722 | 111.9727 | 111.319 | 110.6004 | 110.2758 | 109.9089 | 109.6491 | 109.3333 | 109.0153 | 108.6895 | 108.5768 | 108.4168 | 108.1496 | 107.5751
| 12FP | Water Available For Use (own sources) | 7FP-(10FP) | Ml/d | 2 | 131.2671 | 131.2671 | 131.2671 | 131.2671 | 129.6671 | 129.2671 | 128.8671 | 128.4671 | 128.0671 | 127.6671 | 127.2671 | 126.8671 | 126.4671 | 126.0671 | 125.7671 | 125.6671 | 125.5671 | 125.4671 | 125.3671 | 132.2671 | 132.1671 | 132.0671 | 131.9671 | 131.8671 | 131.7671 | 131.6671 | 131.5671 | 131.4671 | 131.3671
| 13FP | Total Water Available For Use | 12FP+(2FP+3FP)-(5FP+6FP) | Ml/d | 2 | 131.2671 | 131.2671 | 131.2671 | 131.2671 | 129.6671 | 129.2671 | 128.8671 | 128.4671 | 128.0671 | 127.6671 | 127.2671 | 126.8671 | 126.4671 | 126.0671 | 125.7671 | 125.6671 | 125.5671 | 125.4671 | 125.3671 | 132.2671 | 132.1671 | 132.0671 | 131.9671 | 131.8671 | 131.7671 | 131.6671 | 131.5671 | 131.4671 | 131.3671
| 14FP | Target headroom (climate change component) | Input | Ml/d | 2 | 0 | 0.24775 | 0.48499 | 0.7085 | 0.96641 | 1.162 | 1.3439 | 1.6498 | 1.8938 | 1.9159 | 2.1404 | 2.4168 | 2.6475 | 2.9631 | 3.1278 | 3.1258 | 3.2322 | 3.3224 | 3.283 | 3.3923 | 3.4104 | 3.5045 | 3.6565 | 3.6711 | 3.7877 | 4.0262 | 4.25 | 4.5035 | 4.8624
| 15FP | Target headroom (All other components) | Input | Ml/d | 2 | 4.4322 | 4.2288 | 3.9968 | 3.8487 | 3.798 | 3.6527 | 3.5209 | 3.7092 | 3.6483 | 2.8405 | 2.8719 | 3.013 | 3.0031 | 3.1805 | 3.3254 | 3.2621 | 3.342 | 3.277 | 3.3661 | 3.3389 | 3.3704 | 3.5033 | 3.6337 | 3.6186 | 3.6883 | 3.7835 | 3.8788 | 4.0863 | 4.3155
| 16FP | Target Headroom | 14FP+15FP | Ml/d | 2 | 4.4322 | 4.4766 | 4.4817 | 4.5572 | 4.7644 | 4.8147 | 4.8648 | 5.3589 | 5.5421 | 4.7564 | 5.0122 | 5.4298 | 5.6506 | 6.1436 | 6.4532 | 6.3879 | 6.5742 | 6.5994 | 6.6491 | 6.7311 | 6.7808 | 7.0079 | 7.2902 | 7.2897 | 7.476 | 7.8097 | 8.1288 | 8.5897 | 9.1779
| 17FP | Available Headroom | 13FP-11FP | Ml/d | 2 | 8.998 | 9.2877 | 9.6228 | 9.8584 | 8.6166 | 8.392 | 8.5977 | 9.783 | 11.0143 | 10.9994 | 11.253 | 11.4852 | 11.7753 | 11.9586 | 12.3504 | 12.9451 | 13.5944 | 14.1481 | 14.7667 | 21.9913 | 22.2582 | 22.418 | 22.6338 | 22.8518 | 23.0776 | 23.0903 | 23.1503 | 23.3175 | 23.792
| 18FP | Supply Demand Balance | 17FP-16FP | Ml/d | 2 | 4.5658 | 4.8112 | 5.1411 | 5.3011 | 3.8522 | 3.5773 | 3.7329 | 4.4241 | 5.4722 | 6.243 | 6.2408 | 6.0555 | 6.1247 | 5.815 | 5.8972 | 6.5572 | 7.0202 | 7.5486 | 8.1177 | 15.2602 | 15.4775 | 15.4102 | 15.3436 | 15.5621 | 15.6016 | 15.2807 | 15.0215 | 14.7278 | 14.6141
|  | Company: | Severn Trent Water
|  | Resource Zone Name: | North Staffordshire
|  | Resource Zone Number: | 7
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | No more than 3 in 100 Temporary Use Bans

## 10. Drought plan links
Table 10: Drought plan links and Deployable Output Overview
10.1 Planning scenarios |  |  |  |  | 10.2 Water resources management plan | [7 empty] | 10.3 Drought plan | [5 empty] | 10.4 Demand
Drought Scenarios | Drought Description | Drought Severity | Plan in which scenario is used (highlights overlaps) |  | WRMP DO of Sources (not including drought measures) | WRMP Additional Yield from Drought Supply Measures (eg drought permits or orders) |  |  | WRMP Impact on DO of drought plan Demand Restrictions (eg TUBs) |  |  | WRMP DO Levels of Service | Drought Plan Additional Yield from Further Supply Measures (eg drought permits or orders) |  |  | Drought Plan Impact on DO of Further Demand Restrictions (eg TUBs) |  |  | Unrestricted Demand | Restricted Demand
|  |  | WRMP | Drought Plan | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Ml/d | Ml/d
Historic Droughts | 1887-89 | Severe historic drought | Y | n | 136 | (6) | 0 | 0 | (1) | 0 | 136 | 136 | (2) | 0 | 136 | (6) | 0 | 0 | 120.68 | 114.646
| 1933-34 | Severe historic drought | Y | Y | 137 | (6) | 0 | 0 | (1) | 0 | 137 | 137 | (2) | 0 | 137 | (6) | 0 | 0 | 120.68 | 114.646
| 1975-76 | Severe historic drought | Y | Y | 136 | (6) | 0 | 0 | (1) | 0 | 136 | 136 | (2) | 0 | 136 | (6) | 0 | 0 | 120.68 | 114.646
| 1995-96 | TUBs last implemented | Y | Y | 134 | (6) | 0 | 0 | (1) | 0 | 134 | 134 | (2) | 3 | 137 | (6) | 0 | 0 | 120.68 | 114.646
Additional Drought Scenarios | Scenario 141 | 1 in 200 yr 30-month (0.50% chance of occurance) | Y | n | 136 | (6) | 0 | 0 | (1) | 0 | 136 | 136 | (2) | 1 | 137 | (6) | 0 | 0 | 120.68 | 114.646
| Scenario 43 | 1 in 300 yr 18-month (0.33% chance of occurance) | Y | n | 134 | (6) | 0 | 0 | (1) | 0 | 134 | 134 | (2) | 1 | 135 | (6) | 0 | 0 | 120.68 | 114.646
| Scenario 24 | 1 in 500 yr 24-month (0.20% of chance of occurance) | Y | n | 130 | (6) | 0 | 0 | (1) | 0 | 130 | 130 | (2) | 5 | 135 | (6) | 0 | 0 | 120.68 | 114.646
| Scenario 161 | 1 in 1000 yr 24-month (0.10% chance of occurance) | Y | n | 41 | (6) | 0 | 0 | (1) | 0 | 41 | 41 | (2) | 94 | 135 | (6) | 0 | 0 | 120.68 | 114.646
Reported DO for WRMP tables highlighted in yellow
10.5 Summary report
WRMP DO Overview | [8 empty] | Drought Plan Overview
DO Modelling Assumptions- not using emergency storage, each drought event is modelled over a 95-year run with LoS at 1 in 33-years (1 TUBs and 1 NEUBs) for the Demand Restrictions Run. For the North Staffordshire WRZ demand restrictions are applied under TUBs at (5%) and NEUBs (an additional 5%). | [8 empty] | There is a drought permit on the River Churnet outlined in our drought plan with further information availble in the Churnet Drought Permit Environmental Assessment Report
Additional Drought Scenarios | [8 empty] | Drought Supply Measures and Demand Restrictions Further Details
Drought scenarios selected from our drought library of 200 stochastic scenarios. The scenarios presented in the table provide a range of drought severities and durations for plausible events. See Appendix A9 of the dWRMP report for more information on their development. | [8 empty] | List individual measures used in scenario e.g. (1) Demand savings restrictions drought measure (TUBs 5% demand saving and NEUBs additional 5% demand saving assumed) (2) Churnet Drought Permit/Order- reservoir compensation releases reduced to ease reservoir drawdown with increased compensation flows augmented with groundwater input (6) No data entered in these cells- N/A for the WRZ
Impact on Supply Demand
Under the 1 in 1000 year drought scenario DO in the North Staffs WRZ is severely reduced- DO is constrainted by Tittesworth Reservoir reaching emergency storage under both the no drought measures and demand restrictions scenarios. However, under the Churnet drought permit/order modelling scenario DO can be recovered.
Demands
Unrestricted demand based on total vaule summed across all demand centres for the WRZ in our Aquator model restricted demand is based on the value reported for the unrestricted demand with a 5% reduction to account for an assumed 5% demand savings that could be realised through a TUB.